## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 24 | 25 | 19 | 14 | 27.6 | 11.83 | 50 | 85 | 20.6 | 71.2 | 34.5 | 218.6 | 220.9 | 218.6 | YES
2 | OK | 25 | 88 | 19 | 14 | 27.6 | 11.83 | 50 | 85 | 20.6 | 71.2 | 34.5 | 218.6 | 220.9 | 218.6 | YES
3 | OK | 88 | 20 | 19 | 14 | 27.6 | 11.83 | 50 | 85 | 20.6 | 71.2 | 34.4 | 218.6 | 220.9 | 218.6 | YES
| NG | 0 | 4 | 61 | 11 | 73.9 | 37.45 | 50 | 85 | 20.6 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 20.6% (degenerate)
| NG | 4 | 5 | 61 | 11 | 73.9 | 36.03 | 50 | 85 | 20.6 | 42.5 | 64.6 | 223.6 | 209.9 | 209.9 | NO
4 | OK | 5 | 6 | 61 | 11 | 73.9 | 33.47 | 50 | 85 | 20.6 | 45.5 | 61.3 | 223.3 | 211.4 | 211.4 | YES
5 | OK | 6 | 7 | 61 | 11 | 73.9 | 23.37 | 50 | 85 | 20.6 | 57.2 | 48.5 | 221.9 | 214.3 | 214.3 | YES
6 | OK | 6 | 97 | 77 | 11 | 133.1 | 9.78 | 50 | 85 | 20.6 | 73.3 | 32 | 216.7 | 223 | 216.7 | YES
7 | OK | 7 | 8 | 61 | 11 | 73.9 | 16.88 | 50 | 85 | 20.6 | 64.8 | 40.6 | 221.4 | 218.7 | 218.7 | YES
8 | OK | 7 | 47 | 80 | 11 | 106.8 | 6.49 | 50 | 85 | 20.6 | 77.2 | 28.2 | 217.7 | 222.9 | 217.7 | YES
9 | OK | 97 | 83 | 77 | 11 | 133.1 | 9.06 | 50 | 85 | 20.6 | 74.2 | 31.2 | 216.3 | 222.7 | 216.3 | YES
10 | OK | 8 | 9 | 61 | 11 | 73.9 | 12.32 | 50 | 85 | 20.6 | 70.2 | 35.1 | 220.7 | 218.9 | 218.9 | YES
11 | OK | 47 | 48 | 80 | 11 | 106.8 | 6.49 | 50 | 85 | 20.6 | 77.2 | 27.6 | 217.8 | 223.8 | 217.8 | YES
12 | OK | 83 | 81 | 77 | 11 | 133.1 | 9.06 | 50 | 85 | 20.6 | 74.2 | 31.2 | 216.3 | 222.7 | 216.3 | YES
13 | OK | 9 | 12 | 61 | 11 | 73.9 | 12.32 | 50 | 85 | 20.6 | 70.2 | 35.1 | 220.7 | 218.9 | 218.9 | YES
14 | OK | 48 | 49 | 80 | 11 | 106.8 | 5.83 | 50 | 85 | 20.6 | 78 | 27.4 | 217.3 | 223.7 | 217.3 | YES
15 | OK | 81 | 82 | 77 | 11 | 133.1 | 8.56 | 50 | 85 | 20.6 | 74.8 | 30.6 | 216.3 | 223.6 | 216.3 | YES
16 | OK | 12 | 58 | 61 | 11 | 73.9 | 10.36 | 50 | 85 | 20.6 | 72.5 | 32.8 | 220.3 | 218.6 | 218.6 | YES
17 | OK | 49 | 50 | 80 | 11 | 106.8 | 5.83 | 50 | 85 | 20.6 | 78 | 27.4 | 217.3 | 223.7 | 217.3 | YES
18 | OK | 82 | 45 | 77 | 11 | 133.1 | 7.25 | 50 | 85 | 20.6 | 76.3 | 29.1 | 216.4 | 223.5 | 216.4 | YES
19 | OK | 58 | 68 | 61 | 11 | 73.9 | 9.93 | 50 | 85 | 20.6 | 73.1 | 32.4 | 220.2 | 218.4 | 218.4 | YES
20 | OK | 45 | 46 | 77 | 11 | 133.1 | 6.22 | 50 | 85 | 20.6 | 77.5 | 27.8 | 216.4 | 225.3 | 216.4 | YES
21 | ** OPTIMAL ** | 68 | 13 | 61 | 11 | 73.9 | 8.54 | 50 | 85 | 20.6 | 74.7 | 30.6 | 220.2 | 220.7 | 220.2 | YES
22 | OK | 46 | 78 | 77 | 11 | 133.1 | 6.22 | 50 | 85 | 20.6 | 77.5 | 27.8 | 216.4 | 225.3 | 216.4 | YES
23 | OK | 13 | 14 | 61 | 11 | 73.9 | 8.48 | 50 | 85 | 20.6 | 74.8 | 30.6 | 220.1 | 220.7 | 220.1 | YES
24 | OK | 78 | 72 | 77 | 11 | 133.1 | 5.18 | 50 | 85 | 20.6 | 78.8 | 26.6 | 215.8 | 225 | 215.8 | YES
25 | OK | 14 | 59 | 61 | 11 | 73.9 | 8.48 | 50 | 85 | 20.6 | 74.8 | 30.6 | 220.1 | 220.7 | 220.1 | YES
26 | OK | 59 | 60 | 61 | 11 | 73.9 | 8.48 | 50 | 85 | 20.6 | 74.8 | 30.6 | 220.1 | 220.7 | 220.1 | YES
27 | OK | 60 | 66 | 61 | 11 | 73.9 | 8.48 | 50 | 85 | 20.6 | 74.8 | 30.6 | 220.1 | 220.7 | 220.1 | YES
28 | OK | 66 | 15 | 61 | 11 | 73.9 | 8.46 | 50 | 85 | 20.6 | 74.8 | 30.5 | 220.2 | 220.7 | 220.2 | YES
29 | OK | 15 | 16 | 61 | 11 | 73.9 | 8.16 | 50 | 85 | 20.6 | 75.2 | 30.2 | 220 | 220.6 | 220 | YES
| NG | 16 | 17 | 61 | 11 | 73.9 | 8.16 | 50 | 85 | 20.6 | 75.2 | 50.7 | 220 | 15.5 | 15.5 | NO
30 | OK | 17 | 67 | 61 | 11 | 73.9 | 5.72 | 50 | 85 | 20.6 | 78.1 | 27.3 | 219.8 | 223 | 219.8 | YES
31 | OK | 67 | 69 | 61 | 11 | 73.9 | 5.34 | 50 | 85 | 20.6 | 78.5 | 26.8 | 219.8 | 223 | 219.8 | YES
32 | OK | 69 | 63 | 61 | 11 | 73.9 | 5.02 | 50 | 85 | 20.6 | 78.9 | 26.5 | 219.4 | 223.4 | 219.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 49-006945
TR_B (available) | 53-012234
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 85
TR_B Baseline Loading% | 20.6
Total Scenarios Evaluated | 35
Feasible Scenarios | 32
--- Optimal Solution ---
Switch Parent Node | 68
Switch Child Node | 13
Tie Node (TR_A side) | 61
Tie Node (TR_B side) | 11
Tie Line Distance (m) | 73.9
Load Transferred (kW) | 8.54
TR_A Loading After (%) | 74.7
TR_B Loading After (%) | 30.6
Minimum Voltage (V) | 220.2