## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 30 | 54 | 22 | 28 | 22.1 | 78.63 | 50 | 78.1 | 36 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 54 | 53 | 22 | 28 | 22.1 | 77.18 | 50 | 78.1 | 36 | [5 empty] | NO | TR_B sim: not converged
| NG | 53 | 29 | 22 | 28 | 22.1 | 75.13 | 50 | 78.1 | 36 | [5 empty] | NO | TR_B sim: not converged
| NG | 29 | 27 | 22 | 28 | 22.1 | 73.1 | 50 | 78.1 | 36 | [5 empty] | NO | TR_B sim: not converged
| NG | 27 | 47 | 22 | 28 | 22.1 | 49.55 | 50 | 78.1 | 36 | 40.2 | 49.6 | 216.7 | 189.9 | 189.9 | NO
| NG | 47 | 45 | 22 | 28 | 22.1 | 49.02 | 50 | 78.1 | 36 | 40.5 | 49.3 | 216.4 | 191.9 | 191.9 | NO
| NG | 45 | 44 | 22 | 28 | 22.1 | 48.02 | 50 | 78.1 | 36 | 41.3 | 48.7 | 216.4 | 192.5 | 192.5 | NO
| NG | 44 | 25 | 22 | 28 | 22.1 | 46.77 | 50 | 78.1 | 36 | 42.2 | 48 | 216 | 194.8 | 194.8 | NO
| NG | 25 | 17 | 22 | 28 | 22.1 | 46.69 | 50 | 78.1 | 36 | 42.3 | 47.9 | 216 | 195 | 195 | NO
| NG | 17 | 40 | 22 | 28 | 22.1 | 44.42 | 50 | 78.1 | 36 | 43.9 | 47.9 | 216.2 | 195 | 195 | NO
| NG | 40 | 21 | 22 | 28 | 22.1 | 42.09 | 50 | 78.1 | 36 | 45.6 | 46.7 | 215.9 | 197.3 | 197.3 | NO
| NG | 21 | 19 | 22 | 28 | 22.1 | 38.81 | 50 | 78.1 | 36 | 48 | 45.4 | 215.2 | 202.5 | 202.5 | NO
| NG | 19 | 39 | 22 | 28 | 22.1 | 38.03 | 50 | 78.1 | 36 | 48.6 | 45.4 | 215.2 | 202.5 | 202.5 | NO
| NG | 39 | 38 | 22 | 28 | 22.1 | 30.19 | 50 | 78.1 | 36 | 54.4 | 45.4 | 216.1 | 202.5 | 202.5 | NO
| NG | 38 | 65 | 22 | 28 | 22.1 | 29.37 | 50 | 78.1 | 36 | 55.1 | 44.7 | 216.2 | 205.7 | 205.7 | NO
| NG | 65 | 37 | 22 | 28 | 22.1 | 25.11 | 50 | 78.1 | 36 | 58.3 | 43.9 | 215 | 209.9 | 209.9 | NO
1 | OK | 37 | 36 | 22 | 28 | 22.1 | 23.78 | 50 | 78.1 | 36 | 59.3 | 43.7 | 214.9 | 210.8 | 210.8 | YES
2 | ** OPTIMAL ** | 36 | 1 | 22 | 28 | 22.1 | 18.08 | 50 | 78.1 | 36 | 63.8 | 42 | 213.3 | 216 | 213.3 | YES
3 | OK | 1 | 0 | 22 | 28 | 22.1 | 17.82 | 50 | 78.1 | 36 | 64 | 41.9 | 212.9 | 215.9 | 212.9 | YES
| NG | 0 | 13 | 14 | 27 | 137 | 1.03 | 50 | 78.1 | 36 | 75 | 36.3 | 207.2 | 216.7 | 207.2 | NO
| NG | 0 | 35 | 22 | 28 | 22.1 | 13.81 | 50 | 78.1 | 36 | 67.3 | 41.9 | 207.4 | 215.9 | 207.4 | NO
| NG | 35 | 34 | 22 | 28 | 22.1 | 10.97 | 50 | 78.1 | 36 | 68.1 | 41 | 205.9 | 215 | 205.9 | NO
| NG | 34 | 33 | 22 | 28 | 22.1 | 8.96 | 50 | 78.1 | 36 | 71.2 | 40.4 | 204.9 | 214.4 | 204.9 | NO
| NG | 33 | 16 | 22 | 28 | 22.1 | 8.96 | 50 | 78.1 | 36 | 71.2 | 40.4 | 204.9 | 214.4 | 204.9 | NO
| NG | 16 | 15 | 22 | 28 | 22.1 | 8.96 | 50 | 78.1 | 36 | 71.2 | 40.4 | 204.9 | 214.4 | 204.9 | NO
| NG | 15 | 24 | 22 | 28 | 22.1 | 8.92 | 50 | 78.1 | 36 | 71.2 | 40.4 | 204.9 | 214.3 | 204.9 | NO
| NG | 24 | 32 | 22 | 28 | 22.1 | 3.41 | 50 | 78.1 | 36 | 75.4 | 37.7 | 206.2 | 216.7 | 206.2 | NO
| NG | 24 | 86 | 86 | 27 | 42.2 | 5.51 | 50 | 78.1 | 36 | 73.8 | 38.7 | 205.7 | 216.8 | 205.7 | NO
| NG | 32 | 23 | 22 | 28 | 22.1 | 2.64 | 50 | 78.1 | 36 | 76 | 37.3 | 206.5 | 216.7 | 206.5 | NO
| NG | 86 | 87 | 87 | 27 | 81.4 | 3.76 | 50 | 78.1 | 36 | 75.1 | 37.8 | 206.4 | 216.8 | 206.4 | NO
| NG | 23 | 22 | 22 | 28 | 22.1 | 2.64 | 50 | 78.1 | 36 | 76 | 36 | 206.5 | 216.7 | 206.5 | NO
| NG | 87 | 88 | 88 | 27 | 120.8 | 0.22 | 50 | 78.1 | 36 | 77.9 | 36.1 | 207 | 216.7 | 207 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 49-007183
TR_B (available) | 49-005753
TR_A Rated kVA | 160
TR_B Rated kVA | 250
TR_A Baseline Loading% | 78.1
TR_B Baseline Loading% | 36
Total Scenarios Evaluated | 32
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 36
Switch Child Node | 1
Tie Node (TR_A side) | 22
Tie Node (TR_B side) | 28
Tie Line Distance (m) | 22.1
Load Transferred (kW) | 18.08
TR_A Loading After (%) | 63.8
TR_B Loading After (%) | 42
Minimum Voltage (V) | 213.3