## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 41 | 43 | 9 | 6 | 110.4 | 8.13 | 50 | 85.4 | 3.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 43 | 33 | 9 | 6 | 110.4 | 8.13 | 50 | 85.4 | 3.6 | 53.5 | 24.3 | 214.5 | 204.6 | 204.6 | NO
| NG | 33 | 32 | 9 | 6 | 110.4 | 8.13 | 50 | 85.4 | 3.6 | 53.5 | 24.3 | 214.5 | 204.6 | 204.6 | NO
| NG | 32 | 24 | 9 | 6 | 110.4 | 8.13 | 50 | 85.4 | 3.6 | 53.5 | 24.3 | 214.5 | 204.6 | 204.6 | NO
| NG | 24 | 14 | 9 | 6 | 110.4 | 8.01 | 50 | 85.4 | 3.6 | 54 | 23.9 | 214.5 | 205 | 205 | NO
1 | OK | 14 | 13 | 9 | 6 | 110.4 | 4.35 | 50 | 85.4 | 3.6 | 68.1 | 14.1 | 214.5 | 216.4 | 214.5 | YES
2 | ** OPTIMAL ** | 13 | 27 | 9 | 6 | 110.4 | 3.31 | 50 | 85.4 | 3.6 | 72.2 | 11.5 | 214.5 | 219.6 | 214.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 49-010550
TR_B (available) | 27-007627
TR_A Rated kVA | 30
TR_B Rated kVA | 50
TR_A Baseline Loading% | 85.4
TR_B Baseline Loading% | 3.6
Total Scenarios Evaluated | 7
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 13
Switch Child Node | 27
Tie Node (TR_A side) | 9
Tie Node (TR_B side) | 6
Tie Line Distance (m) | 110.4
Load Transferred (kW) | 3.31
TR_A Loading After (%) | 72.2
TR_B Loading After (%) | 11.5
Minimum Voltage (V) | 214.5