## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 41 | 15 | 7 | 1 | 46.8 | 13.64 | 50 | 85.4 | 6.5 | 31.8 | 30 | 218.7 | 205.1 | 205.1 | NO
| NG | 15 | 16 | 7 | 1 | 46.8 | 13.07 | 50 | 85.4 | 6.5 | 34 | 30 | 218.7 | 205.1 | 205.1 | NO
| NG | 16 | 23 | 7 | 1 | 46.8 | 12.39 | 50 | 85.4 | 6.5 | 36.6 | 27.8 | 218.4 | 207.6 | 207.6 | NO
| NG | 23 | 22 | 7 | 1 | 46.8 | 11.32 | 50 | 85.4 | 6.5 | 40.7 | 27.2 | 218.3 | 208.2 | 208.2 | NO
1 | OK | 22 | 21 | 7 | 1 | 46.8 | 9.76 | 50 | 85.4 | 6.5 | 46.7 | 23.6 | 217.7 | 212.2 | 212.2 | YES
2 | OK | 21 | 20 | 7 | 1 | 46.8 | 7.6 | 50 | 85.4 | 6.5 | 55 | 16 | 216.3 | 220.1 | 216.3 | YES
3 | ** OPTIMAL ** | 20 | 3 | 7 | 1 | 46.8 | 7.24 | 50 | 85.4 | 6.5 | 55 | 14.6 | 216.3 | 221.6 | 216.3 | YES
4 | OK | 3 | 8 | 7 | 1 | 46.8 | 5.7 | 50 | 85.4 | 6.5 | 62.5 | 13.8 | 215.8 | 222.4 | 215.8 | YES
5 | OK | 8 | 38 | 7 | 1 | 46.8 | 5.7 | 50 | 85.4 | 6.5 | 62.5 | 13.8 | 215.8 | 222.4 | 215.8 | YES
6 | OK | 38 | 39 | 7 | 1 | 46.8 | 5.58 | 50 | 85.4 | 6.5 | 63 | 13.7 | 215.8 | 222.4 | 215.8 | YES
7 | OK | 39 | 40 | 7 | 1 | 46.8 | 3.25 | 50 | 85.4 | 6.5 | 72.2 | 7.3 | 214.7 | 228.7 | 214.7 | YES
8 | OK | 40 | 4 | 7 | 1 | 46.8 | 3 | 50 | 85.4 | 6.5 | 73.2 | 7.3 | 214.5 | 228.7 | 214.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 49-010550
TR_B (available) | 64-020133
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 85.4
TR_B Baseline Loading% | 6.5
Total Scenarios Evaluated | 12
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 20
Switch Child Node | 3
Tie Node (TR_A side) | 7
Tie Node (TR_B side) | 1
Tie Line Distance (m) | 46.8
Load Transferred (kW) | 7.24
TR_A Loading After (%) | 55
TR_B Loading After (%) | 14.6
Minimum Voltage (V) | 216.3