## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 16 | 8 | 4 | 7 | 125.7 | 5.62 | 50 | 79.6 | 1.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | ** OPTIMAL ** | 8 | 7 | 4 | 7 | 125.7 | 5.12 | 50 | 79.6 | 1.6 | 59.8 | 13.6 | 210.2 | 224 | 210.2 | YES
| NG | 7 | 6 | 4 | 7 | 125.7 | 4.64 | 50 | 79.6 | 1.6 | 61.7 | 11.7 | 209.8 | 225.2 | 209.8 | NO
| NG | 6 | 5 | 4 | 7 | 125.7 | 4.32 | 50 | 79.6 | 1.6 | 62.9 | 11.7 | 209.5 | 225.2 | 209.5 | NO
| NG | 5 | 13 | 4 | 7 | 125.7 | 3.68 | 50 | 79.6 | 1.6 | 65.4 | 10.2 | 209 | 226 | 209 | NO
| NG | 13 | 4 | 4 | 7 | 125.7 | 1.01 | 50 | 79.6 | 1.6 | 75.7 | 4 | 206.8 | 229.4 | 206.8 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 49-014236
TR_B (available) | 49-000241
TR_A Rated kVA | 30
TR_B Rated kVA | 50
TR_A Baseline Loading% | 79.6
TR_B Baseline Loading% | 1.6
Total Scenarios Evaluated | 6
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 8
Switch Child Node | 7
Tie Node (TR_A side) | 4
Tie Node (TR_B side) | 7
Tie Line Distance (m) | 125.7
Load Transferred (kW) | 5.12
TR_A Loading After (%) | 59.8
TR_B Loading After (%) | 13.6
Minimum Voltage (V) | 210.2