## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 16 | 9 | 3 | 14 | 2.1 | 14.68 | 50 | 79.6 | 21.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 9 | 10 | 3 | 14 | 2.1 | 14.16 | 50 | 79.6 | 21.2 | 23.5 | 42.3 | 224.7 | 171.1 | 171.1 | NO
| NG | 10 | 12 | 3 | 14 | 2.1 | 12.14 | 50 | 79.6 | 21.2 | 31.3 | 38.2 | 223.2 | 183.7 | 183.7 | NO
| NG | 12 | 15 | 3 | 14 | 2.1 | 12.14 | 50 | 79.6 | 21.2 | 31.3 | 38.2 | 223.2 | 183.7 | 183.7 | NO
| NG | 15 | 14 | 3 | 14 | 2.1 | 12.07 | 50 | 79.6 | 21.2 | 31.5 | 38.1 | 223.1 | 184.1 | 184.1 | NO
| NG | 14 | 11 | 3 | 14 | 2.1 | 11.54 | 50 | 79.6 | 21.2 | 33.6 | 37.1 | 222.7 | 186.8 | 186.8 | NO
1 | ** OPTIMAL ** | 11 | 0 | 3 | 14 | 2.1 | 3.4 | 50 | 79.6 | 21.2 | 65.6 | 25.2 | 212.2 | 220.2 | 212.2 | YES
2 | OK | 0 | 1 | 3 | 14 | 2.1 | 2.86 | 50 | 79.6 | 21.2 | 67.8 | 24.5 | 211.4 | 221.9 | 211.4 | YES
| NG | 1 | 2 | 3 | 14 | 2.1 | 1.91 | 50 | 79.6 | 21.2 | 71.7 | 23.4 | 209.8 | 224.8 | 209.8 | NO
| NG | 2 | 3 | 3 | 14 | 2.1 | 0.48 | 50 | 79.6 | 21.2 | 77.6 | 21.2 | 206.9 | 6.4 | 6.4 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 49-014236
TR_B (available) | 67-004344
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 79.6
TR_B Baseline Loading% | 21.2
Total Scenarios Evaluated | 10
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 11
Switch Child Node | 0
Tie Node (TR_A side) | 3
Tie Node (TR_B side) | 14
Tie Line Distance (m) | 2.1
Load Transferred (kW) | 3.4
TR_A Loading After (%) | 65.6
TR_B Loading After (%) | 25.2
Minimum Voltage (V) | 212.2