## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 0 | 1 | 16 | 16 | 145.1 | 9.54 | 50 | 82.7 | 45.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 1 | 27 | 16 | 16 | 145.1 | 9.18 | 50 | 82.7 | 45.8 | 47.3 | 75.9 | 221.2 | 213 | 213 | YES
2 | OK | 27 | 32 | 16 | 16 | 145.1 | 7.42 | 50 | 82.7 | 45.8 | 54 | 74.7 | 221 | 213.3 | 213.3 | YES
| NG | 20 | 18 | 15 | 27 | 8.6 | 7.36 | 50 | 82.7 | 45.8 | 54.3 | 64.6 | 221.2 | 204.8 | 204.8 | NO
3 | OK | 32 | 3 | 16 | 16 | 145.1 | 7.13 | 50 | 82.7 | 45.8 | 55.1 | 73.5 | 220.8 | 213.5 | 213.5 | YES
| NG | 18 | 31 | 15 | 27 | 8.6 | 7.36 | 50 | 82.7 | 45.8 | 54.3 | 64.6 | 221.2 | 204.8 | 204.8 | NO
4 | OK | 3 | 4 | 16 | 16 | 145.1 | 5.13 | 50 | 82.7 | 45.8 | 62.8 | 65.6 | 220.2 | 214.2 | 214.2 | YES
| NG | 31 | 30 | 15 | 27 | 8.6 | 6.19 | 50 | 82.7 | 45.8 | 58.7 | 59.5 | 221.2 | 209.6 | 209.6 | NO
5 | OK | 4 | 7 | 16 | 16 | 145.1 | 2.26 | 50 | 82.7 | 45.8 | 73.9 | 54.5 | 219.2 | 215.2 | 215.2 | YES
6 | OK | 30 | 5 | 15 | 27 | 8.6 | 5.4 | 50 | 82.7 | 45.8 | 61.8 | 56.1 | 221.2 | 211.2 | 211.2 | YES
7 | ** OPTIMAL ** | 7 | 8 | 16 | 16 | 145.1 | 1.82 | 50 | 82.7 | 45.8 | 75.6 | 52.8 | 219.2 | 215.2 | 215.2 | YES
8 | OK | 5 | 6 | 15 | 27 | 8.6 | 4.29 | 50 | 82.7 | 45.8 | 66 | 54.3 | 220.7 | 212 | 212 | YES
9 | OK | 6 | 9 | 15 | 27 | 8.6 | 2.93 | 50 | 82.7 | 45.8 | 71.3 | 54.3 | 219.7 | 212 | 212 | YES
10 | OK | 9 | 10 | 15 | 27 | 8.6 | 2.13 | 50 | 82.7 | 45.8 | 74.4 | 54.3 | 219.1 | 212 | 212 | YES
11 | OK | 10 | 11 | 15 | 27 | 8.6 | 2 | 50 | 82.7 | 45.8 | 74.9 | 54 | 219 | 212.1 | 212.1 | YES
12 | OK | 11 | 12 | 15 | 27 | 8.6 | 1.06 | 50 | 82.7 | 45.8 | 78.5 | 50.1 | 219 | 213.8 | 213.8 | YES
13 | OK | 12 | 13 | 15 | 27 | 8.6 | 0.83 | 50 | 82.7 | 45.8 | 79.4 | 49.2 | 219 | 214.2 | 214.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 50-001376
TR_B (available) | 44-001584
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 82.7
TR_B Baseline Loading% | 45.8
Total Scenarios Evaluated | 17
Feasible Scenarios | 13
--- Optimal Solution ---
Switch Parent Node | 7
Switch Child Node | 8
Tie Node (TR_A side) | 16
Tie Node (TR_B side) | 16
Tie Line Distance (m) | 145.1
Load Transferred (kW) | 1.82
TR_A Loading After (%) | 75.6
TR_B Loading After (%) | 52.8
Minimum Voltage (V) | 215.2