## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 0 | 1 | 1 | 39 | 126.7 | 9.54 | 50 | 82.7 | 44.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 1 | 27 | 36 | 39 | 129.5 | 9.18 | 50 | 82.7 | 44.2 | 47.3 | 57.7 | 221.2 | 212.9 | 212.9 | YES
2 | OK | 20 | 19 | 22 | 39 | 9.9 | 4.37 | 50 | 82.7 | 44.2 | 65.9 | 61.4 | 220.5 | 218.5 | 218.5 | YES
| NG | 20 | 18 | 17 | 0 | 30.4 | 7.36 | 50 | 82.7 | 44.2 | 54.3 | 73.9 | 221.2 | 208.4 | 208.4 | NO
3 | ** OPTIMAL ** | 19 | 22 | 22 | 39 | 9.9 | 3.37 | 50 | 82.7 | 44.2 | 69.8 | 57.3 | 219.9 | 220.6 | 219.9 | YES
| NG | 18 | 31 | 31 | 0 | 72.7 | 7.36 | 50 | 82.7 | 44.2 | 54.3 | 73.9 | 221.2 | 208.4 | 208.4 | NO
4 | OK | 22 | 21 | 21 | 39 | 43.4 | 3.23 | 50 | 82.7 | 44.2 | 70.3 | 56.8 | 219.8 | 220.6 | 219.8 | YES
5 | OK | 21 | 23 | 23 | 39 | 81.5 | 2.45 | 50 | 82.7 | 44.2 | 73.3 | 53.7 | 219.2 | 220.2 | 219.2 | YES
6 | OK | 23 | 25 | 25 | 39 | 88.6 | 2.19 | 50 | 82.7 | 44.2 | 74.3 | 52.7 | 218.9 | 220 | 218.9 | YES
7 | OK | 25 | 24 | 24 | 39 | 123.6 | 0.94 | 50 | 82.7 | 44.2 | 79.1 | 47.8 | 218.8 | 222.5 | 218.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 50-001376
TR_B (available) | 63-032419
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 82.7
TR_B Baseline Loading% | 44.2
Total Scenarios Evaluated | 10
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 19
Switch Child Node | 22
Tie Node (TR_A side) | 22
Tie Node (TR_B side) | 39
Tie Line Distance (m) | 9.9
Load Transferred (kW) | 3.37
TR_A Loading After (%) | 69.8
TR_B Loading After (%) | 57.3
Minimum Voltage (V) | 219.9