## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 34 | 1 | 13 | 27 | 1.7 | 19.6 | 50 | 78.5 | 16.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | ** OPTIMAL ** | 1 | 32 | 13 | 27 | 1.7 | 11.14 | 50 | 78.5 | 16.6 | 52.6 | 22 | 216.2 | 212.1 | 212.1 | YES
2 | OK | 32 | 28 | 13 | 27 | 1.7 | 10.39 | 50 | 78.5 | 16.6 | 54.4 | 21.6 | 216.2 | 212 | 212 | YES
3 | OK | 28 | 27 | 13 | 27 | 1.7 | 2.59 | 50 | 78.5 | 16.6 | 72.5 | 17.8 | 211.6 | 216.2 | 211.6 | YES
4 | OK | 27 | 22 | 13 | 27 | 1.7 | 2.47 | 50 | 78.5 | 16.6 | 72.8 | 17.7 | 211.6 | 216.2 | 211.6 | YES
5 | OK | 22 | 21 | 13 | 27 | 1.7 | 2.45 | 50 | 78.5 | 16.6 | 72.8 | 17.7 | 211.6 | 216.2 | 211.6 | YES
6 | OK | 21 | 19 | 13 | 27 | 1.7 | 2.09 | 50 | 78.5 | 16.6 | 73.7 | 17.5 | 211.7 | 216.2 | 211.7 | YES
7 | OK | 19 | 17 | 13 | 27 | 1.7 | 1.82 | 50 | 78.5 | 16.6 | 74.3 | 17.4 | 211.6 | 216.2 | 211.6 | YES
8 | OK | 17 | 15 | 13 | 27 | 1.7 | 1.82 | 50 | 78.5 | 16.6 | 74.3 | 17.4 | 211.6 | 216.2 | 211.6 | YES
9 | OK | 15 | 16 | 18 | 9 | 58.4 | 1.19 | 50 | 78.5 | 16.6 | 75.7 | 16.9 | 211.7 | 215.6 | 211.7 | YES
10 | OK | 15 | 20 | 13 | 27 | 1.7 | 0.58 | 50 | 78.5 | 16.6 | 77.2 | 16.8 | 211.2 | 216.5 | 211.2 | YES
| NG | 16 | 18 | 18 | 9 | 58.4 | 0.29 | 50 | 78.5 | 16.6 | 48.3 | 16.7 | 5.2 | 216.3 | 5.2 | NO
11 | OK | 20 | 14 | 13 | 27 | 1.7 | 0.39 | 50 | 78.5 | 16.6 | 77.6 | 16.7 | 211.2 | 216.5 | 211.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 50-002645
TR_B (available) | 23-011150
TR_A Rated kVA | 50
TR_B Rated kVA | 250
TR_A Baseline Loading% | 78.5
TR_B Baseline Loading% | 16.6
Total Scenarios Evaluated | 13
Feasible Scenarios | 11
--- Optimal Solution ---
Switch Parent Node | 1
Switch Child Node | 32
Tie Node (TR_A side) | 13
Tie Node (TR_B side) | 27
Tie Line Distance (m) | 1.7
Load Transferred (kW) | 11.14
TR_A Loading After (%) | 52.6
TR_B Loading After (%) | 22
Minimum Voltage (V) | 212.1