## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 34 | 23 | 31 | 108 | 65.5 | 14.24 | 50 | 78.5 | 39.7 | [5 empty] | NO | TR_B sim: not converged
| NG | 23 | 24 | 31 | 108 | 65.5 | 6.25 | 50 | 78.5 | 39.7 | 63.8 | 43.5 | 214.6 | 184.6 | 184.6 | NO
| NG | 24 | 25 | 31 | 108 | 65.5 | 5.05 | 50 | 78.5 | 39.7 | 66.6 | 42.7 | 213.9 | 191.7 | 191.7 | NO
| NG | 25 | 26 | 31 | 108 | 65.5 | 2.76 | 50 | 78.5 | 39.7 | 71.9 | 41.2 | 212.7 | 203.5 | 203.5 | NO
1 | OK | 26 | 33 | 31 | 108 | 65.5 | 1.13 | 50 | 78.5 | 39.7 | 75.8 | 40.3 | 211.8 | 210.9 | 210.9 | YES
2 | ** OPTIMAL ** | 33 | 29 | 31 | 108 | 65.5 | 0.42 | 50 | 78.5 | 39.7 | 77.5 | 39.9 | 211.4 | 213 | 211.4 | YES
3 | OK | 29 | 30 | 31 | 108 | 65.5 | 0.2 | 50 | 78.5 | 39.7 | 78 | 39.8 | 211.3 | 213 | 211.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 50-002645
TR_B (available) | 46-003121
TR_A Rated kVA | 50
TR_B Rated kVA | 250
TR_A Baseline Loading% | 78.5
TR_B Baseline Loading% | 39.7
Total Scenarios Evaluated | 7
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 33
Switch Child Node | 29
Tie Node (TR_A side) | 31
Tie Node (TR_B side) | 108
Tie Line Distance (m) | 65.5
Load Transferred (kW) | 0.42
TR_A Loading After (%) | 77.5
TR_B Loading After (%) | 39.9
Minimum Voltage (V) | 211.4