## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 1 | 0 | 2 | 0 | 9.2 | 7.54 | 50 | 78.5 | 61.9 | 58.8 | 80.2 | 214.7 | 210.3 | 210.3 | NO
1 | OK | 0 | 5 | 2 | 0 | 9.2 | 7.47 | 50 | 78.5 | 61.9 | 61.1 | 80 | 214.7 | 210.4 | 210.4 | YES
2 | OK | 5 | 4 | 2 | 0 | 9.2 | 6.78 | 50 | 78.5 | 61.9 | 62.7 | 78.4 | 214.7 | 210.4 | 210.4 | YES
3 | OK | 4 | 10 | 10 | 10 | 103.9 | 5.24 | 50 | 78.5 | 61.9 | 66.2 | 74.5 | 214.7 | 213.9 | 213.9 | YES
4 | OK | 4 | 11 | 2 | 0 | 9.2 | 1.54 | 50 | 78.5 | 61.9 | 75 | 65.5 | 211.2 | 219.1 | 211.2 | YES
5 | ** OPTIMAL ** | 10 | 9 | 9 | 10 | 139.1 | 4.8 | 50 | 78.5 | 61.9 | 67.2 | 73.5 | 214.4 | 214.5 | 214.4 | YES
6 | OK | 11 | 3 | 2 | 0 | 9.2 | 0.64 | 50 | 78.5 | 61.9 | 77 | 63.4 | 211.2 | 219.1 | 211.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 50-002645
TR_B (available) | 58-009068
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 78.5
TR_B Baseline Loading% | 61.9
Total Scenarios Evaluated | 7
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 10
Switch Child Node | 9
Tie Node (TR_A side) | 9
Tie Node (TR_B side) | 10
Tie Line Distance (m) | 139.1
Load Transferred (kW) | 4.8
TR_A Loading After (%) | 67.2
TR_B Loading After (%) | 73.5
Minimum Voltage (V) | 214.4