## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 23 | 18 | 18 | 10 | 69.1 | 4.3 | 50 | 79 | 44 | 68.9 | 61.2 | 216.1 | 211.7 | 211.7 | YES
2 | OK | 23 | 24 | 30 | 11 | 69.8 | 4.84 | 50 | 79 | 44 | 67.7 | 48.4 | 216.6 | 217.1 | 216.6 | YES
3 | OK | 18 | 17 | 22 | 7 | 70.2 | 4.18 | 50 | 79 | 44 | 69.2 | 60.8 | 216.1 | 211.4 | 211.4 | YES
4 | ** OPTIMAL ** | 24 | 27 | 30 | 11 | 69.8 | 3.71 | 50 | 79 | 44 | 67.7 | 44 | 216.6 | 218.4 | 216.6 | YES
5 | OK | 17 | 22 | 22 | 7 | 70.2 | 3.32 | 50 | 79 | 44 | 71.2 | 57.3 | 216.1 | 213 | 213 | YES
6 | OK | 27 | 30 | 30 | 11 | 69.8 | 3.71 | 50 | 79 | 44 | 70.3 | 44 | 216.1 | 218.4 | 216.1 | YES
7 | OK | 22 | 21 | 21 | 7 | 72.7 | 3.29 | 50 | 79 | 44 | 71.3 | 57.2 | 216.1 | 213.3 | 213.3 | YES
| NG | 21 | 20 | 20 | 7 | 74.9 | 3.29 | 50 | 79 | 44 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 44.0% (degenerate)
8 | OK | 20 | 19 | 19 | 13 | 75.4 | 3.29 | 50 | 79 | 44 | 71.3 | 51.3 | 216.1 | 215.2 | 215.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 50-002769
TR_B (available) | 48-003209
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 79
TR_B Baseline Loading% | 44
Total Scenarios Evaluated | 9
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 24
Switch Child Node | 27
Tie Node (TR_A side) | 30
Tie Node (TR_B side) | 11
Tie Line Distance (m) | 69.8
Load Transferred (kW) | 3.71
TR_A Loading After (%) | 67.7
TR_B Loading After (%) | 44
Minimum Voltage (V) | 216.6