## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 7 | 6 | 31 | 43 | 12.6 | 14.85 | 50 | 79 | 11.1 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 6 | 14 | 31 | 43 | 12.6 | 14.26 | 50 | 79 | 11.1 | 45.9 | 11.5 | 216.7 | 228 | 216.7 | YES
2 | ** OPTIMAL ** | 14 | 5 | 31 | 43 | 12.6 | 14.26 | 50 | 79 | 11.1 | 45.9 | 11.5 | 216.7 | 228 | 216.7 | YES
3 | OK | 5 | 4 | 31 | 43 | 12.6 | 13.79 | 50 | 79 | 11.1 | 47 | 11.4 | 216.6 | 228 | 216.6 | YES
4 | OK | 4 | 32 | 31 | 43 | 12.6 | 13.44 | 50 | 79 | 11.1 | 47.8 | 11.4 | 216.6 | 228 | 216.6 | YES
5 | OK | 32 | 23 | 31 | 43 | 12.6 | 13.44 | 50 | 79 | 11.1 | 47.8 | 11.4 | 216.6 | 228 | 216.6 | YES
6 | OK | 23 | 24 | 31 | 43 | 12.6 | 4.84 | 50 | 79 | 11.1 | 67.7 | 11.4 | 216.6 | 228 | 216.6 | YES
7 | OK | 24 | 27 | 31 | 43 | 12.6 | 3.71 | 50 | 79 | 11.1 | 67.7 | 11.1 | 216.6 | 228.1 | 216.6 | YES
8 | OK | 27 | 30 | 31 | 43 | 12.6 | 3.71 | 50 | 79 | 11.1 | 70.3 | 11.1 | 216.1 | 228.1 | 216.1 | YES
9 | OK | 30 | 2 | 31 | 43 | 12.6 | 0.87 | 50 | 79 | 11.1 | 77 | 11.1 | 216.1 | 228.1 | 216.1 | YES
| NG | 2 | 3 | 31 | 43 | 12.6 | 0.87 | 50 | 79 | 11.1 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 11.1% (degenerate)
10 | OK | 3 | 31 | 31 | 43 | 12.6 | 0.01 | 50 | 79 | 11.1 | 79 | 11.1 | 216.1 | 228.1 | 216.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 50-002769
TR_B (available) | 62-000078
TR_A Rated kVA | 50
TR_B Rated kVA | 400
TR_A Baseline Loading% | 79
TR_B Baseline Loading% | 11.1
Total Scenarios Evaluated | 12
Feasible Scenarios | 10
--- Optimal Solution ---
Switch Parent Node | 14
Switch Child Node | 5
Tie Node (TR_A side) | 31
Tie Node (TR_B side) | 43
Tie Line Distance (m) | 12.6
Load Transferred (kW) | 14.26
TR_A Loading After (%) | 45.9
TR_B Loading After (%) | 11.5
Minimum Voltage (V) | 216.7