## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 7 | 6 | 19 | 46 | 3.1 | 14.85 | 50 | 79 | 31.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 7 | 8 | 16 | 11 | 114 | 19.14 | 50 | 79 | 31.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 6 | 14 | 19 | 46 | 3.1 | 14.26 | 50 | 79 | 31.5 | 45.9 | 41.7 | 216.7 | 212 | 212 | YES
| NG | 8 | 9 | 16 | 11 | 114 | 16.66 | 50 | 79 | 31.5 | 40.1 | 40.2 | 222.1 | 195.8 | 195.8 | NO
2 | OK | 14 | 5 | 19 | 46 | 3.1 | 14.26 | 50 | 79 | 31.5 | 45.9 | 41.7 | 216.7 | 212 | 212 | YES
| NG | 9 | 10 | 16 | 11 | 114 | 14.84 | 50 | 79 | 31.5 | 44.3 | 39.1 | 222.1 | 200.3 | 200.3 | NO
3 | OK | 5 | 4 | 19 | 46 | 3.1 | 13.79 | 50 | 79 | 31.5 | 47 | 41.7 | 216.6 | 212 | 212 | YES
| NG | 10 | 11 | 16 | 11 | 114 | 14.29 | 50 | 79 | 31.5 | 45.5 | 39.1 | 222.1 | 200.3 | 200.3 | NO
4 | OK | 4 | 32 | 19 | 46 | 3.1 | 13.44 | 50 | 79 | 31.5 | 47.8 | 41.3 | 216.6 | 212.7 | 212.7 | YES
| NG | 11 | 12 | 16 | 11 | 114 | 13.75 | 50 | 79 | 31.5 | 46.8 | 39.1 | 221.8 | 200.3 | 200.3 | NO
5 | OK | 32 | 23 | 19 | 46 | 3.1 | 13.44 | 50 | 79 | 31.5 | 47.8 | 41.3 | 216.6 | 212.7 | 212.7 | YES
| NG | 12 | 33 | 16 | 11 | 114 | 5.7 | 50 | 79 | 31.5 | 65.5 | 39.1 | 217.9 | 200.3 | 200.3 | NO
6 | OK | 23 | 18 | 19 | 46 | 3.1 | 4.3 | 50 | 79 | 31.5 | 68.9 | 36.6 | 216.1 | 220.9 | 216.1 | YES
7 | OK | 23 | 24 | 29 | 46 | 112.8 | 4.84 | 50 | 79 | 31.5 | 67.7 | 37.2 | 216.6 | 218.6 | 216.6 | YES
| NG | 33 | 15 | 16 | 11 | 114 | 5.7 | 50 | 79 | 31.5 | 65.5 | 39.1 | 217.9 | 200.3 | 200.3 | NO
8 | OK | 18 | 17 | 19 | 46 | 3.1 | 4.18 | 50 | 79 | 31.5 | 69.2 | 36.4 | 216.1 | 221.1 | 216.1 | YES
9 | ** OPTIMAL ** | 24 | 27 | 27 | 46 | 132.8 | 3.71 | 50 | 79 | 31.5 | 67.7 | 35.9 | 216.6 | 218.5 | 216.6 | YES
| NG | 15 | 0 | 16 | 11 | 114 | 5.7 | 50 | 79 | 31.5 | 65.5 | 39.1 | 217.9 | 200.3 | 200.3 | NO
10 | OK | 17 | 22 | 19 | 46 | 3.1 | 3.32 | 50 | 79 | 31.5 | 71.2 | 35.4 | 216.1 | 221.1 | 216.1 | YES
| NG | 0 | 1 | 16 | 11 | 114 | 4.16 | 50 | 79 | 31.5 | 69.1 | 36.8 | 217.9 | 207.6 | 207.6 | NO
11 | OK | 22 | 21 | 19 | 46 | 3.1 | 3.29 | 50 | 79 | 31.5 | 71.3 | 35.4 | 216.1 | 221.1 | 216.1 | YES
12 | OK | 1 | 13 | 16 | 11 | 114 | 2.38 | 50 | 79 | 31.5 | 73.2 | 33.7 | 217.9 | 216.6 | 216.6 | YES
| NG | 21 | 20 | 19 | 46 | 3.1 | 3.29 | 50 | 79 | 31.5 | 71.3 | 1803.4 | 216.1 | 186 | 186 | NO
13 | OK | 13 | 16 | 16 | 11 | 114 | 1.79 | 50 | 79 | 31.5 | 74.7 | 33.7 | 217.9 | 216.6 | 216.6 | YES
14 | OK | 20 | 19 | 19 | 46 | 3.1 | 3.29 | 50 | 79 | 31.5 | 71.3 | 33.6 | 216.1 | 221 | 216.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 50-002769
TR_B (available) | 63-027952
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 79
TR_B Baseline Loading% | 31.5
Total Scenarios Evaluated | 25
Feasible Scenarios | 14
--- Optimal Solution ---
Switch Parent Node | 24
Switch Child Node | 27
Tie Node (TR_A side) | 27
Tie Node (TR_B side) | 46
Tie Line Distance (m) | 132.8
Load Transferred (kW) | 3.71
TR_A Loading After (%) | 67.7
TR_B Loading After (%) | 35.9
Minimum Voltage (V) | 216.6