## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 81 | 87 | 61 | 37 | 4 | 20.31 | 50 | 81.3 | 10.4 | 32 | 18.8 | 217.2 | 223.3 | 217.2 | YES
2 | OK | 87 | 68 | 61 | 37 | 4 | 20.31 | 50 | 81.3 | 10.4 | 32 | 18.8 | 217.2 | 223.3 | 217.2 | YES
3 | OK | 68 | 75 | 61 | 37 | 4 | 17.74 | 50 | 81.3 | 10.4 | 37.9 | 18.8 | 217.2 | 223.3 | 217.2 | YES
4 | OK | 75 | 57 | 61 | 37 | 4 | 17.56 | 50 | 81.3 | 10.4 | 37.9 | 18.8 | 217.2 | 223.3 | 217.2 | YES
5 | OK | 57 | 56 | 61 | 37 | 4 | 17.56 | 50 | 81.3 | 10.4 | 38.3 | 18.8 | 217.2 | 223.3 | 217.2 | YES
6 | OK | 56 | 74 | 61 | 37 | 4 | 17.56 | 50 | 81.3 | 10.4 | 38.3 | 18.8 | 217.2 | 223.3 | 217.2 | YES
7 | OK | 74 | 73 | 61 | 37 | 4 | 17.56 | 50 | 81.3 | 10.4 | 38.3 | 18.8 | 217.2 | 223.3 | 217.2 | YES
8 | OK | 73 | 72 | 61 | 37 | 4 | 17.56 | 50 | 81.3 | 10.4 | 38.3 | 18.8 | 217.2 | 223.3 | 217.2 | YES
9 | ** OPTIMAL ** | 72 | 78 | 61 | 37 | 4 | 17.56 | 50 | 81.3 | 10.4 | 38.3 | 18.8 | 217.2 | 223.3 | 217.2 | YES
10 | OK | 78 | 84 | 61 | 37 | 4 | 17.47 | 50 | 81.3 | 10.4 | 38.5 | 18.8 | 217.2 | 223.3 | 217.2 | YES
11 | OK | 84 | 77 | 61 | 37 | 4 | 17.22 | 50 | 81.3 | 10.4 | 39.1 | 17.8 | 217.1 | 224.1 | 217.1 | YES
12 | OK | 77 | 18 | 61 | 37 | 4 | 17.22 | 50 | 81.3 | 10.4 | 39.1 | 17.8 | 217.1 | 224.1 | 217.1 | YES
13 | OK | 18 | 17 | 61 | 37 | 4 | 16.48 | 50 | 81.3 | 10.4 | 40.8 | 14.9 | 216.7 | 226.2 | 216.7 | YES
| NG | 17 | 34 | 38 | 36 | 33 | 9.11 | 50 | 81.3 | 10.4 | 58.5 | 49.1 | 211.1 | 199.7 | 199.7 | NO
| NG | 17 | 71 | 61 | 37 | 4 | 7.37 | 50 | 81.3 | 10.4 | 63.5 | 14.9 | 204.7 | 226.2 | 204.7 | NO
| NG | 34 | 90 | 38 | 36 | 33 | 8.75 | 50 | 81.3 | 10.4 | 59.3 | 47.4 | 211.3 | 201 | 201 | NO
| NG | 71 | 85 | 61 | 37 | 4 | 7.37 | 50 | 81.3 | 10.4 | 63.5 | 14.9 | 204.7 | 226.2 | 204.7 | NO
| NG | 90 | 65 | 38 | 36 | 33 | 1.35 | 50 | 81.3 | 10.4 | 77.7 | 15.6 | 207.2 | 226 | 207.2 | NO
| NG | 85 | 59 | 61 | 37 | 4 | 7.29 | 50 | 81.3 | 10.4 | 63.7 | 14.6 | 204.7 | 226.4 | 204.7 | NO
| NG | 65 | 35 | 38 | 36 | 33 | 0.99 | 50 | 81.3 | 10.4 | 78.6 | 14.2 | 206.2 | 227 | 206.2 | NO
| NG | 59 | 58 | 61 | 37 | 4 | 6.21 | 50 | 81.3 | 10.4 | 321.8 | 10.4 | 20.5 | 229.3 | 20.5 | NO
| NG | 35 | 36 | 38 | 36 | 33 | 0.99 | 50 | 81.3 | 10.4 | 78.6 | 14.2 | 206.2 | 227 | 206.2 | NO
| NG | 58 | 42 | 61 | 37 | 4 | 6.21 | 50 | 81.3 | 10.4 | 66.2 | 10.4 | 205.2 | 229.3 | 205.2 | NO
| NG | 42 | 41 | 61 | 37 | 4 | 5.65 | 50 | 81.3 | 10.4 | 67.7 | 10.4 | 203.7 | 229.3 | 203.7 | NO
| NG | 41 | 51 | 51 | 37 | 94.3 | 5.07 | 50 | 81.3 | 10.4 | 69.3 | 31 | 202.2 | 212.5 | 202.2 | NO
| NG | 51 | 64 | 62 | 8 | 122.2 | 4.19 | 50 | 81.3 | 10.4 | 71.3 | 27.3 | 202.3 | 215.5 | 202.3 | NO
| NG | 64 | 63 | 62 | 8 | 122.2 | 3.31 | 50 | 81.3 | 10.4 | 73.3 | 23.6 | 202.4 | 218.6 | 202.4 | NO
| NG | 63 | 62 | 62 | 8 | 122.2 | 2.39 | 50 | 81.3 | 10.4 | 75.5 | 19.8 | 202.5 | 221.6 | 202.5 | NO
| NG | 62 | 52 | 52 | 8 | 134.5 | 2.39 | 50 | 81.3 | 10.4 | 75.5 | 19.8 | 202.5 | 221.9 | 202.5 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 50-003083
TR_B (available) | 51-003669
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 81.3
TR_B Baseline Loading% | 10.4
Total Scenarios Evaluated | 29
Feasible Scenarios | 13
--- Optimal Solution ---
Switch Parent Node | 72
Switch Child Node | 78
Tie Node (TR_A side) | 61
Tie Node (TR_B side) | 37
Tie Line Distance (m) | 4
Load Transferred (kW) | 17.56
TR_A Loading After (%) | 38.3
TR_B Loading After (%) | 18.8
Minimum Voltage (V) | 217.2