## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 22 | 23 | 43 | 2 | 167.6 | 11.03 | 50 | 77 | 26.1 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 23 | 25 | 43 | 2 | 167.6 | 11.03 | 50 | 77 | 26.1 | 51.4 | 31.8 | 215.7 | 216.2 | 215.7 | YES
2 | ** OPTIMAL ** | 25 | 24 | 43 | 2 | 167.6 | 10.93 | 50 | 77 | 26.1 | 51.6 | 31.5 | 215.7 | 216.6 | 215.7 | YES
3 | OK | 24 | 36 | 43 | 2 | 167.6 | 3.62 | 50 | 77 | 26.1 | 68.6 | 27.7 | 214.3 | 222.5 | 214.3 | YES
4 | OK | 36 | 37 | 43 | 2 | 167.6 | 3.51 | 50 | 77 | 26.1 | 68.8 | 27.7 | 214.3 | 222.5 | 214.3 | YES
5 | OK | 37 | 29 | 43 | 2 | 167.6 | 3.26 | 50 | 77 | 26.1 | 69.4 | 27.1 | 214.4 | 223.3 | 214.4 | YES
6 | OK | 29 | 28 | 43 | 2 | 167.6 | 0.36 | 50 | 77 | 26.1 | 76.1 | 26.9 | 213.8 | 223.5 | 213.8 | YES
7 | OK | 28 | 27 | 43 | 2 | 167.6 | 0.36 | 50 | 77 | 26.1 | 76.1 | 26.9 | 213.8 | 223.5 | 213.8 | YES
8 | OK | 27 | 43 | 43 | 2 | 167.6 | 0.04 | 50 | 77 | 26.1 | 76.9 | 26.1 | 213.8 | 224.4 | 213.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 50-004137
TR_B (available) | 46-005725
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 77
TR_B Baseline Loading% | 26.1
Total Scenarios Evaluated | 9
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 25
Switch Child Node | 24
Tie Node (TR_A side) | 43
Tie Node (TR_B side) | 2
Tie Line Distance (m) | 167.6
Load Transferred (kW) | 10.93
TR_A Loading After (%) | 51.6
TR_B Loading After (%) | 31.5
Minimum Voltage (V) | 215.7