## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 22 | 23 | 34 | 28 | 20.9 | 11.03 | 50 | 77 | 46.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 23 | 25 | 34 | 28 | 20.9 | 11.03 | 50 | 77 | 46.7 | 51.4 | 73 | 215.7 | 215.3 | 215.3 | YES
2 | OK | 45 | 26 | 16 | 39 | 8.1 | 9.67 | 50 | 77 | 46.7 | 54.4 | 70.1 | 216.2 | 210.9 | 210.9 | YES
3 | OK | 25 | 24 | 34 | 28 | 20.9 | 10.93 | 50 | 77 | 46.7 | 51.6 | 72.8 | 215.7 | 215.3 | 215.3 | YES
4 | OK | 26 | 3 | 16 | 39 | 8.1 | 9.24 | 50 | 77 | 46.7 | 55.3 | 69 | 216.2 | 213 | 213 | YES
5 | OK | 24 | 36 | 36 | 40 | 112.5 | 3.62 | 50 | 77 | 46.7 | 68.6 | 55.2 | 214.3 | 222.1 | 214.3 | YES
6 | OK | 24 | 55 | 34 | 28 | 20.9 | 7.31 | 50 | 77 | 46.7 | 59.9 | 64 | 215.2 | 216.5 | 215.2 | YES
7 | OK | 3 | 2 | 16 | 39 | 8.1 | 7.7 | 50 | 77 | 46.7 | 58.9 | 65.1 | 216.2 | 217.9 | 216.2 | YES
8 | OK | 36 | 37 | 37 | 41 | 122.4 | 3.51 | 50 | 77 | 46.7 | 68.8 | 54.9 | 214.3 | 222.5 | 214.3 | YES
9 | OK | 55 | 35 | 34 | 28 | 20.9 | 7.31 | 50 | 77 | 46.7 | 59.9 | 64 | 215.2 | 216.5 | 215.2 | YES
10 | OK | 2 | 13 | 16 | 39 | 8.1 | 7.7 | 50 | 77 | 46.7 | 58.9 | 65.1 | 216.2 | 217.9 | 216.2 | YES
11 | OK | 37 | 29 | 29 | 41 | 138.1 | 3.26 | 50 | 77 | 46.7 | 69.4 | 54.4 | 214.4 | 222.6 | 214.4 | YES
12 | OK | 35 | 31 | 34 | 28 | 20.9 | 6.06 | 50 | 77 | 46.7 | 62.8 | 61 | 215 | 217.3 | 215 | YES
13 | OK | 13 | 1 | 16 | 39 | 8.1 | 7.25 | 50 | 77 | 46.7 | 59.9 | 64 | 216.2 | 218.2 | 216.2 | YES
14 | OK | 29 | 28 | 28 | 41 | 140 | 0.36 | 50 | 77 | 46.7 | 76.1 | 47.6 | 213.8 | 224.4 | 213.8 | YES
15 | OK | 31 | 32 | 34 | 28 | 20.9 | 5.46 | 50 | 77 | 46.7 | 64.2 | 59.7 | 215 | 217.2 | 215 | YES
16 | ** OPTIMAL ** | 1 | 0 | 16 | 39 | 8.1 | 6.72 | 50 | 77 | 46.7 | 61.1 | 62.7 | 216.2 | 218.5 | 216.2 | YES
17 | OK | 28 | 27 | 27 | 42 | 158.8 | 0.36 | 50 | 77 | 46.7 | 76.1 | 47.6 | 213.8 | 224.4 | 213.8 | YES
18 | OK | 32 | 40 | 34 | 28 | 20.9 | 5.32 | 50 | 77 | 46.7 | 64.5 | 59.3 | 215 | 217.2 | 215 | YES
19 | OK | 0 | 14 | 16 | 39 | 8.1 | 6.4 | 50 | 77 | 46.7 | 61.9 | 62 | 216 | 219.7 | 216 | YES
20 | OK | 27 | 43 | 43 | 42 | 173.8 | 0.04 | 50 | 77 | 46.7 | 76.9 | 46.8 | 213.8 | 224.4 | 213.8 | YES
21 | OK | 40 | 39 | 34 | 28 | 20.9 | 3.54 | 50 | 77 | 46.7 | 68.6 | 55.1 | 215 | 216.6 | 215 | YES
22 | OK | 14 | 15 | 16 | 39 | 8.1 | 5.91 | 50 | 77 | 46.7 | 63 | 60.8 | 215.8 | 219.6 | 215.8 | YES
23 | OK | 39 | 34 | 34 | 28 | 20.9 | 3.23 | 50 | 77 | 46.7 | 69.3 | 54.4 | 214.9 | 216.9 | 214.9 | YES
24 | OK | 15 | 17 | 17 | 39 | 146.6 | 3.11 | 50 | 77 | 46.7 | 69.7 | 54.1 | 213.7 | 220.3 | 213.7 | YES
25 | OK | 15 | 46 | 16 | 39 | 8.1 | 2.8 | 50 | 77 | 46.7 | 70.3 | 53.3 | 215.6 | 221.1 | 215.6 | YES
26 | OK | 34 | 33 | 33 | 28 | 21.1 | 2.68 | 50 | 77 | 46.7 | 70.6 | 53.1 | 214.9 | 216.9 | 214.9 | YES
27 | OK | 17 | 18 | 18 | 39 | 158.7 | 2.49 | 50 | 77 | 46.7 | 71.1 | 52.6 | 213.8 | 219.9 | 213.8 | YES
28 | OK | 46 | 47 | 16 | 39 | 8.1 | 2.8 | 50 | 77 | 46.7 | 70.3 | 52.1 | 215.6 | 221 | 215.6 | YES
29 | OK | 33 | 53 | 53 | 9 | 134.6 | 2.68 | 50 | 77 | 46.7 | 70.6 | 48.3 | 214.9 | 224.4 | 214.9 | YES
30 | OK | 47 | 16 | 16 | 39 | 8.1 | 1.97 | 50 | 77 | 46.7 | 72.2 | 51.4 | 215.5 | 221.8 | 215.5 | YES
31 | OK | 53 | 54 | 54 | 9 | 147.2 | 2.66 | 50 | 77 | 46.7 | 70.7 | 48.3 | 214.9 | 224.4 | 214.9 | YES
32 | OK | 16 | 12 | 12 | 39 | 44.5 | 0.97 | 50 | 77 | 46.7 | 74.7 | 49 | 213.9 | 224.1 | 213.9 | YES
33 | OK | 12 | 11 | 11 | 39 | 84.2 | 0.58 | 50 | 77 | 46.7 | 75.6 | 48.1 | 214 | 223.9 | 214 | YES
34 | OK | 11 | 10 | 10 | 1 | 116.9 | 0.45 | 50 | 77 | 46.7 | 75.9 | 47.8 | 213.5 | 224.1 | 213.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 50-004137
TR_B (available) | 49-012029
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 77
TR_B Baseline Loading% | 46.7
Total Scenarios Evaluated | 35
Feasible Scenarios | 34
--- Optimal Solution ---
Switch Parent Node | 1
Switch Child Node | 0
Tie Node (TR_A side) | 16
Tie Node (TR_B side) | 39
Tie Line Distance (m) | 8.1
Load Transferred (kW) | 6.72
TR_A Loading After (%) | 61.1
TR_B Loading After (%) | 62.7
Minimum Voltage (V) | 216.2