## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 35 | 34 | 55 | 27 | 1.3 | 30.91 | 50 | 65.8 | 38.1 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 34 | 33 | 32 | 4 | 148.6 | 0.95 | 50 | 65.8 | 38.1 | 63.9 | 38.8 | 218.4 | 225.2 | 218.4 | YES
| NG | 34 | 1 | 55 | 27 | 1.3 | 29.81 | 50 | 65.8 | 38.1 | 31.3 | 60.1 | 223.5 | 207.6 | 207.6 | NO
2 | OK | 33 | 32 | 32 | 4 | 148.6 | 0.45 | 50 | 65.8 | 38.1 | 65.3 | 38.1 | 218.4 | 225.2 | 218.4 | YES
| NG | 1 | 2 | 55 | 27 | 1.3 | 19.88 | 50 | 65.8 | 38.1 | 42.7 | 53.2 | 223.3 | 206.8 | 206.8 | NO
3 | OK | 1 | 3 | 0 | 12 | 7.9 | 9.35 | 95 | 65.8 | 38.1 | 55 | 44.9 | 218.5 | 222.2 | 218.5 | YES
4 | ** OPTIMAL ** | 2 | 12 | 55 | 27 | 1.3 | 5.75 | 50 | 65.8 | 38.1 | 59.1 | 41.3 | 219.9 | 225.2 | 219.9 | YES
5 | OK | 3 | 75 | 0 | 12 | 7.9 | 9.2 | 95 | 65.8 | 38.1 | 55.2 | 44.8 | 218.5 | 222.3 | 218.5 | YES
6 | OK | 12 | 10 | 55 | 27 | 1.3 | 4.36 | 50 | 65.8 | 38.1 | 60.7 | 41.2 | 219.8 | 225.2 | 219.8 | YES
7 | OK | 75 | 74 | 0 | 12 | 7.9 | 8.11 | 95 | 65.8 | 38.1 | 56.4 | 44 | 218.3 | 222.3 | 218.3 | YES
8 | OK | 10 | 11 | 55 | 27 | 1.3 | 4.36 | 50 | 65.8 | 38.1 | 60.7 | 41.2 | 219.8 | 225.2 | 219.8 | YES
9 | OK | 74 | 72 | 0 | 12 | 7.9 | 7.47 | 95 | 65.8 | 38.1 | 57.2 | 43.5 | 218.3 | 222.2 | 218.3 | YES
10 | OK | 11 | 8 | 55 | 27 | 1.3 | 4.36 | 50 | 65.8 | 38.1 | 60.7 | 41.1 | 219.8 | 225.2 | 219.8 | YES
11 | OK | 72 | 73 | 31 | 9 | 50.1 | 7.41 | 50 | 65.8 | 38.1 | 57.2 | 42.4 | 218.3 | 222.4 | 218.3 | YES
12 | OK | 72 | 83 | 0 | 12 | 7.9 | 0.06 | 95 | 65.8 | 38.1 | 65.7 | 38.1 | 218.4 | 225.2 | 218.4 | YES
13 | OK | 8 | 9 | 55 | 27 | 1.3 | 4.23 | 50 | 65.8 | 38.1 | 60.9 | 41.1 | 219.8 | 225.2 | 219.8 | YES
14 | OK | 73 | 30 | 31 | 9 | 50.1 | 6.08 | 50 | 65.8 | 38.1 | 58.8 | 42.4 | 218.3 | 222.4 | 218.3 | YES
15 | OK | 83 | 4 | 0 | 12 | 7.9 | 0.06 | 95 | 65.8 | 38.1 | 65.7 | 38.1 | 218.4 | 225.2 | 218.4 | YES
16 | OK | 9 | 59 | 55 | 27 | 1.3 | 4.08 | 50 | 65.8 | 38.1 | 61 | 41 | 219.7 | 225.2 | 219.7 | YES
17 | OK | 30 | 29 | 31 | 9 | 50.1 | 4.66 | 50 | 65.8 | 38.1 | 60.4 | 41.5 | 218.3 | 223.4 | 218.3 | YES
18 | OK | 4 | 0 | 0 | 12 | 7.9 | 0.06 | 95 | 65.8 | 38.1 | 65.7 | 38.1 | 218.4 | 225.2 | 218.4 | YES
19 | OK | 59 | 57 | 55 | 27 | 1.3 | 2.52 | 50 | 65.8 | 38.1 | 62.8 | 39.9 | 219.2 | 225.2 | 219.2 | YES
20 | OK | 29 | 5 | 31 | 9 | 50.1 | 4.66 | 50 | 65.8 | 38.1 | 60.4 | 41.5 | 218.3 | 223.4 | 218.3 | YES
21 | OK | 57 | 76 | 55 | 27 | 1.3 | 2.13 | 50 | 65.8 | 38.1 | 62.8 | 39.6 | 219.2 | 225.2 | 219.2 | YES
22 | OK | 5 | 6 | 31 | 9 | 50.1 | 4.6 | 50 | 65.8 | 38.1 | 60.4 | 41.5 | 218.3 | 223.4 | 218.3 | YES
23 | OK | 76 | 77 | 55 | 27 | 1.3 | 0.15 | 50 | 65.8 | 38.1 | 65.6 | 38.2 | 218.4 | 225.2 | 218.4 | YES
24 | OK | 6 | 7 | 31 | 9 | 50.1 | 2.44 | 50 | 65.8 | 38.1 | 63 | 39.9 | 218.3 | 224.5 | 218.3 | YES
25 | OK | 77 | 56 | 55 | 27 | 1.3 | 0.15 | 50 | 65.8 | 38.1 | 65.6 | 38.2 | 218.5 | 225.2 | 218.5 | YES
| NG | 7 | 31 | 31 | 9 | 50.1 | 1.56 | 50 | 65.8 | 38.1 | 64 | 328.1 | 218.4 | 18 | 18 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 50-005685
TR_B (available) | 59-018450
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 65.8
TR_B Baseline Loading% | 38.1
Total Scenarios Evaluated | 29
Feasible Scenarios | 25
--- Optimal Solution ---
Switch Parent Node | 2
Switch Child Node | 12
Tie Node (TR_A side) | 55
Tie Node (TR_B side) | 27
Tie Line Distance (m) | 1.3
Load Transferred (kW) | 5.75
TR_A Loading After (%) | 59.1
TR_B Loading After (%) | 41.3
Minimum Voltage (V) | 219.9