## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 35 | 34 | 28 | 16 | 30 | 30.91 | 50 | 65.8 | 27.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 35 | 70 | 48 | 16 | 50.2 | 26.02 | 50 | 65.8 | 27.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 34 | 33 | 33 | 21 | 98.3 | 0.95 | 50 | 65.8 | 27.9 | 63.9 | 27.9 | 218.4 | 225.6 | 218.4 | YES
| NG | 34 | 1 | 28 | 16 | 30 | 29.81 | 50 | 65.8 | 27.9 | 31.3 | 36.4 | 223.5 | 202.3 | 202.3 | NO
| NG | 70 | 68 | 48 | 16 | 50.2 | 26.02 | 50 | 65.8 | 27.9 | 35.8 | 34.9 | 221.6 | 209 | 209 | NO
2 | OK | 33 | 32 | 32 | 21 | 102.7 | 0.45 | 50 | 65.8 | 27.9 | 65.3 | 27.9 | 218.4 | 225.6 | 218.4 | YES
| NG | 1 | 2 | 28 | 16 | 30 | 19.88 | 50 | 65.8 | 27.9 | 42.7 | 35.9 | 223.3 | 203.8 | 203.8 | NO
3 | OK | 1 | 3 | 83 | 28 | 59.5 | 9.35 | 50 | 65.8 | 27.9 | 55 | 32.4 | 218.5 | 216.5 | 216.5 | YES
4 | OK | 68 | 71 | 48 | 16 | 50.2 | 22.32 | 50 | 65.8 | 27.9 | 40 | 33.8 | 221.1 | 212.2 | 212.2 | YES
5 | OK | 2 | 13 | 28 | 16 | 30 | 14.13 | 50 | 65.8 | 27.9 | 49.3 | 33.5 | 222.3 | 212.4 | 212.4 | YES
6 | OK | 2 | 12 | 58 | 28 | 40.1 | 5.75 | 50 | 65.8 | 27.9 | 59.1 | 28.1 | 219.9 | 225.6 | 219.9 | YES
7 | OK | 3 | 75 | 83 | 28 | 59.5 | 9.2 | 50 | 65.8 | 27.9 | 55.2 | 32.3 | 218.5 | 216.8 | 216.8 | YES
8 | OK | 71 | 36 | 48 | 16 | 50.2 | 20.97 | 50 | 65.8 | 27.9 | 41.5 | 33.1 | 220.8 | 213.9 | 213.9 | YES
9 | OK | 13 | 14 | 16 | 20 | 79.9 | 1.48 | 50 | 65.8 | 27.9 | 64.1 | 28.6 | 219 | 223.9 | 219 | YES
10 | OK | 13 | 18 | 28 | 16 | 30 | 11.93 | 50 | 65.8 | 27.9 | 51.9 | 32.8 | 222 | 214.7 | 214.7 | YES
11 | OK | 12 | 10 | 58 | 28 | 40.1 | 4.36 | 50 | 65.8 | 27.9 | 60.7 | 28.1 | 219.8 | 225.6 | 219.8 | YES
12 | OK | 75 | 74 | 83 | 28 | 59.5 | 8.11 | 50 | 65.8 | 27.9 | 56.4 | 31.8 | 218.3 | 216.8 | 216.8 | YES
13 | OK | 36 | 37 | 48 | 16 | 50.2 | 14.57 | 50 | 65.8 | 27.9 | 48.9 | 32.4 | 220.5 | 215.3 | 215.3 | YES
14 | OK | 36 | 40 | 43 | 21 | 93.4 | 6.4 | 50 | 65.8 | 27.9 | 58.4 | 28.5 | 218.7 | 224.6 | 218.7 | YES
15 | OK | 18 | 17 | 28 | 16 | 30 | 11.93 | 50 | 65.8 | 27.9 | 51.9 | 32.8 | 222 | 214.7 | 214.7 | YES
16 | OK | 10 | 11 | 58 | 28 | 40.1 | 4.36 | 50 | 65.8 | 27.9 | 60.7 | 28.1 | 219.8 | 225.6 | 219.8 | YES
17 | OK | 74 | 72 | 83 | 28 | 59.5 | 7.47 | 50 | 65.8 | 27.9 | 57.2 | 31.5 | 218.3 | 216.6 | 216.6 | YES
18 | OK | 37 | 44 | 44 | 16 | 65.2 | 5.1 | 50 | 65.8 | 27.9 | 59.9 | 28.6 | 218.7 | 224.8 | 218.7 | YES
19 | OK | 37 | 47 | 48 | 16 | 50.2 | 9.47 | 50 | 65.8 | 27.9 | 54.8 | 31.7 | 220.2 | 217.1 | 217.1 | YES
20 | OK | 40 | 38 | 43 | 21 | 93.4 | 6 | 50 | 65.8 | 27.9 | 58.9 | 28.5 | 218.7 | 224.6 | 218.7 | YES
21 | OK | 17 | 64 | 28 | 16 | 30 | 11.03 | 50 | 65.8 | 27.9 | 52.9 | 32.3 | 221.8 | 216 | 216 | YES
22 | OK | 11 | 8 | 58 | 28 | 40.1 | 4.36 | 50 | 65.8 | 27.9 | 60.7 | 28.1 | 219.8 | 225.6 | 219.8 | YES
23 | OK | 72 | 73 | 73 | 28 | 87.2 | 7.41 | 50 | 65.8 | 27.9 | 57.2 | 31.5 | 218.3 | 217.1 | 217.1 | YES
24 | OK | 72 | 83 | 83 | 28 | 59.5 | 0.06 | 50 | 65.8 | 27.9 | 65.7 | 27.9 | 218.4 | 225.6 | 218.4 | YES
25 | OK | 44 | 45 | 45 | 16 | 94.3 | 4.62 | 50 | 65.8 | 27.9 | 60.5 | 28.3 | 218.6 | 225.4 | 218.6 | YES
26 | OK | 47 | 48 | 48 | 16 | 50.2 | 9.12 | 50 | 65.8 | 27.9 | 55.2 | 31.5 | 220.1 | 217.5 | 217.5 | YES
27 | OK | 38 | 39 | 43 | 21 | 93.4 | 1 | 50 | 65.8 | 27.9 | 64.6 | 28.4 | 218.6 | 224.9 | 218.6 | YES
28 | OK | 38 | 41 | 60 | 21 | 106.4 | 5 | 50 | 65.8 | 27.9 | 60 | 28 | 218.4 | 225.6 | 218.4 | YES
29 | OK | 64 | 63 | 28 | 16 | 30 | 8.96 | 50 | 65.8 | 27.9 | 55.3 | 31.7 | 221.5 | 217.7 | 217.7 | YES
30 | OK | 8 | 9 | 58 | 28 | 40.1 | 4.23 | 50 | 65.8 | 27.9 | 60.9 | 28.1 | 219.8 | 225.6 | 219.8 | YES
31 | OK | 73 | 30 | 30 | 28 | 93 | 6.08 | 50 | 65.8 | 27.9 | 58.8 | 30.9 | 218.3 | 216.6 | 216.6 | YES
32 | OK | 83 | 4 | 4 | 37 | 61.5 | 0.06 | 50 | 65.8 | 27.9 | 65.7 | 27.9 | 218.4 | 225.6 | 218.4 | YES
33 | OK | 45 | 46 | 46 | 16 | 128.6 | 3.64 | 50 | 65.8 | 27.9 | 61.6 | 27.9 | 218.4 | 225.6 | 218.4 | YES
34 | OK | 48 | 49 | 49 | 16 | 60.3 | 8.02 | 50 | 65.8 | 27.9 | 56.4 | 31 | 219.9 | 218.7 | 218.7 | YES
35 | OK | 48 | 86 | 86 | 16 | 56.1 | 1.1 | 50 | 65.8 | 27.9 | 64.5 | 28.4 | 218.7 | 225.4 | 218.7 | YES
| NG | 39 | 43 | 43 | 21 | 93.4 | 1 | 50 | 65.8 | 27.9 | 64.6 | 81.5 | 218.6 | 19.7 | 19.7 | NO
36 | OK | 41 | 42 | 60 | 21 | 106.4 | 0.22 | 50 | 65.8 | 27.9 | 65.5 | 28 | 218.4 | 225.6 | 218.4 | YES
37 | OK | 63 | 20 | 28 | 16 | 30 | 8.02 | 50 | 65.8 | 27.9 | 56.4 | 31.6 | 221.5 | 217.9 | 217.9 | YES
38 | OK | 9 | 59 | 58 | 28 | 40.1 | 4.08 | 50 | 65.8 | 27.9 | 61 | 28.1 | 219.7 | 225.6 | 219.7 | YES
39 | OK | 30 | 29 | 29 | 28 | 111.7 | 4.66 | 50 | 65.8 | 27.9 | 60.4 | 30.2 | 218.3 | 218.5 | 218.3 | YES
40 | OK | 4 | 0 | 0 | 26 | 74.1 | 0.06 | 50 | 65.8 | 27.9 | 65.7 | 27.9 | 218.4 | 225.6 | 218.4 | YES
41 | OK | 49 | 50 | 50 | 16 | 77.7 | 5.18 | 50 | 65.8 | 27.9 | 59.7 | 29.8 | 219.4 | 221.4 | 219.4 | YES
42 | OK | 86 | 61 | 61 | 16 | 57.5 | 1.1 | 50 | 65.8 | 27.9 | 64.5 | 28.4 | 218.7 | 225.4 | 218.7 | YES
43 | OK | 42 | 60 | 60 | 21 | 106.4 | 0.12 | 50 | 65.8 | 27.9 | 65.7 | 27.9 | 218.4 | 225.6 | 218.4 | YES
44 | ** OPTIMAL ** | 20 | 19 | 28 | 16 | 30 | 5.94 | 50 | 65.8 | 27.9 | 58.8 | 30.5 | 221 | 220.6 | 220.6 | YES
45 | OK | 59 | 57 | 76 | 37 | 41.3 | 2.52 | 50 | 65.8 | 27.9 | 62.8 | 29.1 | 219.2 | 223.3 | 219.2 | YES
46 | OK | 29 | 5 | 6 | 28 | 115.3 | 4.66 | 50 | 65.8 | 27.9 | 60.4 | 30.1 | 218.3 | 219.4 | 218.3 | YES
47 | OK | 50 | 51 | 51 | 16 | 89.5 | 4.19 | 50 | 65.8 | 27.9 | 60.9 | 29.8 | 219.4 | 221.4 | 219.4 | YES
48 | OK | 61 | 62 | 62 | 16 | 80.9 | 0.55 | 50 | 65.8 | 27.9 | 65.2 | 28.1 | 218.5 | 225.6 | 218.5 | YES
49 | OK | 19 | 65 | 28 | 16 | 30 | 3.95 | 50 | 65.8 | 27.9 | 61.1 | 29.6 | 220.6 | 222.8 | 220.6 | YES
50 | OK | 57 | 76 | 76 | 37 | 41.3 | 2.13 | 50 | 65.8 | 27.9 | 62.8 | 28.9 | 219.2 | 223.3 | 219.2 | YES
51 | OK | 5 | 6 | 6 | 28 | 115.3 | 4.6 | 50 | 65.8 | 27.9 | 60.4 | 30.1 | 218.3 | 219.5 | 218.3 | YES
52 | OK | 51 | 52 | 52 | 16 | 105.5 | 3.41 | 50 | 65.8 | 27.9 | 61.8 | 29.5 | 219.2 | 222.2 | 219.2 | YES
53 | OK | 62 | 84 | 84 | 16 | 94.5 | 0.55 | 50 | 65.8 | 27.9 | 65.2 | 28.1 | 218.5 | 225.6 | 218.5 | YES
54 | OK | 65 | 25 | 28 | 16 | 30 | 3.95 | 50 | 65.8 | 27.9 | 61.1 | 29.5 | 220.6 | 222.9 | 220.6 | YES
55 | OK | 76 | 77 | 78 | 26 | 44.6 | 0.15 | 50 | 65.8 | 27.9 | 65.6 | 28 | 218.4 | 225.5 | 218.4 | YES
56 | OK | 6 | 7 | 7 | 28 | 117 | 2.44 | 50 | 65.8 | 27.9 | 63 | 29.1 | 218.3 | 222.8 | 218.3 | YES
57 | OK | 52 | 53 | 53 | 16 | 119.6 | 0.72 | 50 | 65.8 | 27.9 | 64.9 | 28.2 | 218.6 | 225.6 | 218.6 | YES
58 | OK | 25 | 22 | 28 | 16 | 30 | 3.49 | 50 | 65.8 | 27.9 | 61.6 | 29.5 | 220.6 | 222.9 | 220.6 | YES
59 | OK | 77 | 56 | 56 | 26 | 46.5 | 0.15 | 50 | 65.8 | 27.9 | 65.6 | 28 | 218.5 | 225.5 | 218.5 | YES
| NG | 7 | 31 | 31 | 28 | 117.5 | 1.56 | 50 | 65.8 | 27.9 | 64 | 2.4 | 218.4 | 6.2 | 6.2 | NO
60 | OK | 22 | 23 | 23 | 16 | 39.9 | 0.51 | 50 | 65.8 | 27.9 | 65.2 | 27.9 | 218.7 | 225.6 | 218.7 | YES
61 | OK | 22 | 26 | 28 | 16 | 30 | 1.03 | 50 | 65.8 | 27.9 | 64.6 | 28.4 | 219.6 | 225.4 | 219.6 | YES
62 | OK | 26 | 28 | 28 | 16 | 30 | 1.03 | 50 | 65.8 | 27.9 | 64.6 | 28.4 | 219.6 | 225.4 | 219.6 | YES
63 | OK | 28 | 85 | 85 | 16 | 44.5 | 1.03 | 50 | 65.8 | 27.9 | 64.6 | 28.4 | 219.6 | 225.5 | 219.6 | YES
64 | OK | 85 | 21 | 21 | 16 | 61.1 | 0.9 | 50 | 65.8 | 27.9 | 64.7 | 28.3 | 219.5 | 225.6 | 219.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 50-005685
TR_B (available) | 66-016976
TR_A Rated kVA | 100
TR_B Rated kVA | 250
TR_A Baseline Loading% | 65.8
TR_B Baseline Loading% | 27.9
Total Scenarios Evaluated | 71
Feasible Scenarios | 64
--- Optimal Solution ---
Switch Parent Node | 20
Switch Child Node | 19
Tie Node (TR_A side) | 28
Tie Node (TR_B side) | 16
Tie Line Distance (m) | 30
Load Transferred (kW) | 5.94
TR_A Loading After (%) | 58.8
TR_B Loading After (%) | 30.5
Minimum Voltage (V) | 220.6