## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 7 | 28 | 26 | 11 | 38.8 | 11.72 | 50 | 83.1 | 38.1 | 37.5 | 52.2 | 222 | 213.8 | 213.8 | YES
2 | OK | 28 | 29 | 26 | 11 | 38.8 | 11.72 | 50 | 83.1 | 38.1 | 37.5 | 52 | 222 | 214.4 | 214.4 | YES
3 | OK | 29 | 48 | 26 | 11 | 38.8 | 11.35 | 50 | 83.1 | 38.1 | 38.9 | 51.7 | 221.8 | 214.2 | 214.2 | YES
4 | OK | 48 | 8 | 26 | 11 | 38.8 | 10.91 | 50 | 83.1 | 38.1 | 38.9 | 51.1 | 221.8 | 215.8 | 215.8 | YES
5 | OK | 8 | 9 | 26 | 11 | 38.8 | 10.91 | 50 | 83.1 | 38.1 | 40.6 | 51.1 | 221.8 | 215.8 | 215.8 | YES
6 | OK | 9 | 10 | 26 | 11 | 38.8 | 10.29 | 50 | 83.1 | 38.1 | 42.9 | 50.4 | 221.8 | 216.2 | 216.2 | YES
7 | OK | 10 | 27 | 26 | 11 | 38.8 | 10 | 50 | 83.1 | 38.1 | 44 | 50 | 221.6 | 216.2 | 216.2 | YES
8 | OK | 27 | 40 | 26 | 11 | 38.8 | 10 | 50 | 83.1 | 38.1 | 44 | 48 | 221.6 | 216.4 | 216.4 | YES
9 | OK | 40 | 23 | 26 | 11 | 38.8 | 8.4 | 50 | 83.1 | 38.1 | 50.2 | 48 | 221 | 216.4 | 216.4 | YES
10 | OK | 23 | 24 | 26 | 11 | 38.8 | 7.62 | 50 | 83.1 | 38.1 | 53.1 | 47.1 | 220.9 | 216.5 | 216.5 | YES
11 | OK | 24 | 42 | 26 | 11 | 38.8 | 7.07 | 50 | 83.1 | 38.1 | 54.1 | 46.4 | 220.9 | 216.7 | 216.7 | YES
12 | OK | 42 | 43 | 26 | 11 | 38.8 | 4.75 | 50 | 83.1 | 38.1 | 64.2 | 43.6 | 220.1 | 217 | 217 | YES
13 | OK | 43 | 13 | 26 | 11 | 38.8 | 4.72 | 50 | 83.1 | 38.1 | 64.4 | 43.6 | 220.1 | 217 | 217 | YES
14 | OK | 13 | 14 | 26 | 11 | 38.8 | 4.02 | 50 | 83.1 | 38.1 | 67.1 | 42.8 | 220.1 | 217.1 | 217.1 | YES
15 | OK | 14 | 15 | 26 | 11 | 38.8 | 4.02 | 50 | 83.1 | 38.1 | 67.1 | 42.8 | 220.1 | 217.1 | 217.1 | YES
16 | OK | 15 | 16 | 26 | 11 | 38.8 | 4.02 | 50 | 83.1 | 38.1 | 67.1 | 42.8 | 220.1 | 217.1 | 217.1 | YES
17 | OK | 16 | 17 | 26 | 11 | 38.8 | 4.02 | 50 | 83.1 | 38.1 | 67.1 | 42.8 | 220.1 | 217.1 | 217.1 | YES
18 | OK | 17 | 46 | 26 | 11 | 38.8 | 2.25 | 50 | 83.1 | 38.1 | 74 | 40.7 | 219.1 | 217.3 | 217.3 | YES
19 | ** OPTIMAL ** | 46 | 25 | 26 | 11 | 38.8 | 2.22 | 50 | 83.1 | 38.1 | 74.1 | 40.7 | 219 | 217.3 | 217.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 50-007019
TR_B (available) | 26-008841
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 83.1
TR_B Baseline Loading% | 38.1
Total Scenarios Evaluated | 19
Feasible Scenarios | 19
--- Optimal Solution ---
Switch Parent Node | 46
Switch Child Node | 25
Tie Node (TR_A side) | 26
Tie Node (TR_B side) | 11
Tie Line Distance (m) | 38.8
Load Transferred (kW) | 2.22
TR_A Loading After (%) | 74.1
TR_B Loading After (%) | 40.7
Minimum Voltage (V) | 217.3