## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 4 | 22 | 18 | 32 | 58 | 6.82 | 50 | 83.1 | 64.2 | 56.6 | 78.1 | 216.3 | 206 | 206 | NO
1 | OK | 22 | 21 | 18 | 32 | 58 | 3.24 | 50 | 83.1 | 64.2 | 70.2 | 72.2 | 215.4 | 214 | 214 | YES
2 | OK | 21 | 3 | 18 | 32 | 58 | 3.24 | 50 | 83.1 | 64.2 | 70.4 | 72.2 | 215.4 | 214 | 214 | YES
3 | OK | 3 | 2 | 18 | 32 | 58 | 2.39 | 50 | 83.1 | 64.2 | 73.7 | 70.1 | 215.2 | 216.5 | 215.2 | YES
4 | OK | 2 | 1 | 18 | 32 | 58 | 0.98 | 50 | 83.1 | 64.2 | 79.2 | 66.6 | 215 | 217.4 | 215 | YES
| NG | 23 | 24 | 25 | 35 | 143.8 | 7.62 | 50 | 83.1 | 64.2 | 53.1 | 75.7 | 220.9 | 209.5 | 209.5 | NO
5 | OK | 24 | 42 | 25 | 35 | 143.8 | 7.07 | 50 | 83.1 | 64.2 | 54.1 | 74.3 | 220.9 | 211.8 | 211.8 | YES
6 | OK | 42 | 43 | 25 | 35 | 143.8 | 4.75 | 50 | 83.1 | 64.2 | 64.2 | 71 | 220.1 | 217 | 217 | YES
7 | OK | 43 | 13 | 25 | 35 | 143.8 | 4.72 | 50 | 83.1 | 64.2 | 64.4 | 70.9 | 220.1 | 217.1 | 217.1 | YES
8 | ** OPTIMAL ** | 13 | 14 | 25 | 35 | 143.8 | 4.02 | 50 | 83.1 | 64.2 | 67.1 | 69.2 | 220.1 | 219.4 | 219.4 | YES
9 | OK | 14 | 15 | 25 | 35 | 143.8 | 4.02 | 50 | 83.1 | 64.2 | 67.1 | 69.2 | 220.1 | 219.4 | 219.4 | YES
10 | OK | 15 | 16 | 25 | 35 | 143.8 | 4.02 | 50 | 83.1 | 64.2 | 67.1 | 69.2 | 220.1 | 219.4 | 219.4 | YES
11 | OK | 16 | 17 | 25 | 35 | 143.8 | 4.02 | 50 | 83.1 | 64.2 | 67.1 | 69.2 | 220.1 | 219.4 | 219.4 | YES
12 | OK | 17 | 46 | 25 | 35 | 143.8 | 2.25 | 50 | 83.1 | 64.2 | 74 | 67.6 | 219.1 | 220 | 219.1 | YES
13 | OK | 46 | 25 | 25 | 35 | 143.8 | 2.22 | 50 | 83.1 | 64.2 | 74.1 | 67.5 | 219 | 220 | 219 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 50-007019
TR_B (available) | 49-012198
TR_A Rated kVA | 30
TR_B Rated kVA | 50
TR_A Baseline Loading% | 83.1
TR_B Baseline Loading% | 64.2
Total Scenarios Evaluated | 15
Feasible Scenarios | 13
--- Optimal Solution ---
Switch Parent Node | 13
Switch Child Node | 14
Tie Node (TR_A side) | 25
Tie Node (TR_B side) | 35
Tie Line Distance (m) | 143.8
Load Transferred (kW) | 4.02
TR_A Loading After (%) | 67.1
TR_B Loading After (%) | 69.2
Minimum Voltage (V) | 219.4