## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 7 | 6 | 11 | 0 | 13 | 9.71 | 50 | 83.1 | 39 | 45.5 | 76.8 | 217.8 | 215.5 | 215.5 | YES
2 | OK | 7 | 28 | 28 | 8 | 80.8 | 11.72 | 50 | 83.1 | 39 | 37.5 | 56.5 | 222 | 216.1 | 216.1 | YES
3 | OK | 6 | 12 | 11 | 0 | 13 | 9.14 | 50 | 83.1 | 39 | 47.7 | 74.5 | 217.6 | 215.7 | 215.7 | YES
4 | OK | 28 | 29 | 29 | 8 | 85.4 | 11.72 | 50 | 83.1 | 39 | 37.5 | 56.5 | 222 | 216.1 | 216.1 | YES
5 | OK | 12 | 11 | 11 | 0 | 13 | 8.91 | 50 | 83.1 | 39 | 48.6 | 73.6 | 217.4 | 215.7 | 215.7 | YES
6 | OK | 29 | 48 | 48 | 8 | 93.2 | 11.35 | 50 | 83.1 | 39 | 38.9 | 55.7 | 221.8 | 216.2 | 216.2 | YES
7 | OK | 11 | 5 | 5 | 0 | 25.8 | 8.91 | 50 | 83.1 | 39 | 48.6 | 73.6 | 217.4 | 215.7 | 215.7 | YES
8 | OK | 48 | 8 | 8 | 8 | 95.4 | 10.91 | 50 | 83.1 | 39 | 38.9 | 55.7 | 221.8 | 216.2 | 216.2 | YES
9 | OK | 5 | 4 | 4 | 0 | 59.7 | 7.95 | 50 | 83.1 | 39 | 52.3 | 69.8 | 217.1 | 216.2 | 216.2 | YES
10 | OK | 8 | 9 | 9 | 8 | 117.4 | 10.91 | 50 | 83.1 | 39 | 40.6 | 55.7 | 221.8 | 216.2 | 216.2 | YES
11 | OK | 4 | 22 | 22 | 0 | 70.1 | 6.82 | 50 | 83.1 | 39 | 56.6 | 60.3 | 216.3 | 217.2 | 216.3 | YES
12 | OK | 9 | 10 | 10 | 8 | 166.4 | 10.29 | 50 | 83.1 | 39 | 42.9 | 55.7 | 221.8 | 216.2 | 216.2 | YES
13 | OK | 22 | 38 | 38 | 0 | 82.8 | 2.22 | 50 | 83.1 | 39 | 74.4 | 47.6 | 215.2 | 218.7 | 215.2 | YES
14 | OK | 22 | 21 | 21 | 0 | 74 | 3.24 | 50 | 83.1 | 39 | 70.2 | 51.5 | 215.4 | 218.1 | 215.4 | YES
15 | ** OPTIMAL ** | 10 | 27 | 27 | 8 | 196.8 | 10 | 50 | 83.1 | 39 | 44 | 54.5 | 221.6 | 216.5 | 216.5 | YES
16 | OK | 38 | 41 | 41 | 0 | 102.6 | 2.07 | 50 | 83.1 | 39 | 74.9 | 47 | 215.1 | 218.7 | 215.1 | YES
17 | OK | 21 | 3 | 3 | 8 | 100.9 | 3.24 | 50 | 83.1 | 39 | 70.4 | 46.2 | 215.4 | 218.1 | 215.4 | YES
18 | OK | 41 | 19 | 19 | 0 | 132.4 | 1.68 | 50 | 83.1 | 39 | 76.5 | 45.5 | 214.8 | 218.7 | 214.8 | YES
19 | OK | 3 | 2 | 2 | 8 | 136.8 | 2.39 | 50 | 83.1 | 39 | 73.7 | 44.1 | 215.2 | 218.5 | 215.2 | YES
20 | OK | 19 | 20 | 20 | 0 | 188.5 | 1.57 | 50 | 83.1 | 39 | 76.9 | 45.1 | 214.8 | 218.7 | 214.8 | YES
21 | OK | 2 | 1 | 1 | 8 | 172.2 | 0.98 | 50 | 83.1 | 39 | 79.2 | 39.8 | 215 | 219.4 | 215 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 50-007019
TR_B (available) | 60-022024
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 83.1
TR_B Baseline Loading% | 39
Total Scenarios Evaluated | 21
Feasible Scenarios | 21
--- Optimal Solution ---
Switch Parent Node | 10
Switch Child Node | 27
Tie Node (TR_A side) | 27
Tie Node (TR_B side) | 8
Tie Line Distance (m) | 196.8
Load Transferred (kW) | 10
TR_A Loading After (%) | 44
TR_B Loading After (%) | 54.5
Minimum Voltage (V) | 216.5