## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | ** OPTIMAL ** | 24 | 2 | 2 | 46 | 62.7 | 1.14 | 50 | 81.8 | 60.9 | 77.3 | 60.9 | 216.8 | 213.2 | 213.2 | YES
| NG | 2 | 42 | 42 | 46 | 69.5 | 0.97 | 50 | 81.8 | 60.9 | [5 empty] | NO | TR_A sim: loading inf% (degenerate)
2 | OK | 42 | 41 | 41 | 46 | 96.7 | 0.97 | 50 | 81.8 | 60.9 | 77.3 | 64.7 | 216.8 | 212.4 | 212.4 | YES
| NG | 41 | 17 | 17 | 46 | 99.9 | 0.64 | 50 | 81.8 | 60.9 | [5 empty] | NO | TR_A sim: loading inf% (degenerate)
3 | OK | 17 | 16 | 16 | 46 | 124.2 | 0.59 | 50 | 81.8 | 60.9 | 77.3 | 63.2 | 216.8 | 212.7 | 212.7 | YES
4 | OK | 16 | 94 | 94 | 46 | 127 | 0.59 | 50 | 81.8 | 60.9 | 77.3 | 63.2 | 216.8 | 212.7 | 212.7 | YES
5 | OK | 94 | 91 | 91 | 46 | 134.5 | 0.59 | 50 | 81.8 | 60.9 | 77.3 | 63.2 | 216.8 | 212.7 | 212.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 51-002097
TR_B (available) | 60-008313
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 81.8
TR_B Baseline Loading% | 60.9
Total Scenarios Evaluated | 7
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 24
Switch Child Node | 2
Tie Node (TR_A side) | 2
Tie Node (TR_B side) | 46
Tie Line Distance (m) | 62.7
Load Transferred (kW) | 1.14
TR_A Loading After (%) | 77.3
TR_B Loading After (%) | 60.9
Minimum Voltage (V) | 213.2