## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 2 | 3 | 7 | 5 | 3.7 | 12.6 | 50 | 89.7 | 20.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 2 | 8 | 15 | 74 | 47.3 | 10.5 | 50 | 89.7 | 20.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | ** OPTIMAL ** | 3 | 10 | 7 | 5 | 3.7 | 7.59 | 50 | 89.7 | 20.7 | 60.6 | 24.4 | 213.9 | 216.5 | 213.9 | YES
| NG | 8 | 15 | 15 | 74 | 47.3 | 10.5 | 50 | 89.7 | 20.7 | 48.1 | 26.1 | 225.1 | 205.7 | 205.7 | NO
2 | OK | 10 | 6 | 7 | 5 | 3.7 | 4.18 | 50 | 89.7 | 20.7 | 71.4 | 22.8 | 211.7 | 217 | 211.7 | YES
| NG | 15 | 14 | 4 | 27 | 47.7 | 10.49 | 50 | 89.7 | 20.7 | 48.2 | 26.4 | 225.1 | 195.8 | 195.8 | NO
| NG | 14 | 13 | 4 | 27 | 47.7 | 10.49 | 50 | 89.7 | 20.7 | 48.2 | 26.4 | 225.1 | 195.8 | 195.8 | NO
| NG | 13 | 12 | 4 | 27 | 47.7 | 10.47 | 50 | 89.7 | 20.7 | 48.2 | 26.4 | 225.1 | 196 | 196 | NO
| NG | 12 | 18 | 4 | 27 | 47.7 | 10.47 | 50 | 89.7 | 20.7 | 48.2 | 26.4 | 225.1 | 196 | 196 | NO
| NG | 18 | 17 | 4 | 27 | 47.7 | 10.45 | 50 | 89.7 | 20.7 | 48.3 | 26.4 | 225.1 | 196.1 | 196.1 | NO
| NG | 17 | 16 | 4 | 27 | 47.7 | 10.45 | 50 | 89.7 | 20.7 | 48.3 | 26.4 | 225.1 | 196.1 | 196.1 | NO
| NG | 16 | 1 | 4 | 27 | 47.7 | 8.68 | 50 | 89.7 | 20.7 | 55.1 | 25.4 | 222 | 195.2 | 195.2 | NO
| NG | 1 | 0 | 4 | 27 | 47.7 | 8.3 | 50 | 89.7 | 20.7 | 56.6 | 25.2 | 222.1 | 197.2 | 197.2 | NO
| NG | 0 | 9 | 4 | 27 | 47.7 | 6.31 | 50 | 89.7 | 20.7 | 64.3 | 24 | 221.2 | 206.8 | 206.8 | NO
3 | OK | 9 | 5 | 4 | 27 | 47.7 | 3.7 | 50 | 89.7 | 20.7 | 74.7 | 22.6 | 217 | 213.6 | 213.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 51-002117
TR_B (available) | 57-010175
TR_A Rated kVA | 30
TR_B Rated kVA | 250
TR_A Baseline Loading% | 89.7
TR_B Baseline Loading% | 20.7
Total Scenarios Evaluated | 15
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 3
Switch Child Node | 10
Tie Node (TR_A side) | 7
Tie Node (TR_B side) | 5
Tie Line Distance (m) | 3.7
Load Transferred (kW) | 7.59
TR_A Loading After (%) | 60.6
TR_B Loading After (%) | 24.4
Minimum Voltage (V) | 213.9