## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 22 | 20 | 59 | 12 | 3.5 | 4.24 | 50 | 20.5 | 19.5 | 18.4 | 29.4 | 221.4 | 219 | 219 | YES
2 | OK | 20 | 21 | 59 | 12 | 3.5 | 3.57 | 50 | 20.5 | 19.5 | 19.6 | 29.4 | 221.1 | 219 | 219 | YES
3 | OK | 21 | 32 | 59 | 12 | 3.5 | 2.88 | 50 | 20.5 | 19.5 | 19.6 | 29.4 | 221.1 | 219 | 219 | YES
4 | OK | 32 | 33 | 59 | 12 | 3.5 | 0.38 | 50 | 20.5 | 19.5 | 19.6 | 19.5 | 221.1 | 225.2 | 221.1 | YES
5 | OK | 32 | 56 | 56 | 12 | 98.1 | 2.5 | 50 | 20.5 | 19.5 | 20.5 | 29.4 | 220.9 | 219.1 | 219.1 | YES
6 | OK | 33 | 58 | 59 | 12 | 3.5 | 0.38 | 50 | 20.5 | 19.5 | 19.6 | 19.5 | 221.1 | 225.2 | 221.1 | YES
7 | OK | 56 | 19 | 19 | 12 | 134.6 | 1.3 | 50 | 20.5 | 19.5 | 20.5 | 24.6 | 220.9 | 222.1 | 220.9 | YES
8 | ** OPTIMAL ** | 58 | 59 | 59 | 12 | 3.5 | 0.38 | 50 | 20.5 | 19.5 | 19.6 | 19.5 | 221.1 | 225.2 | 221.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 51-005349
TR_B (available) | 60-020453
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 20.5
TR_B Baseline Loading% | 19.5
Total Scenarios Evaluated | 8
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 58
Switch Child Node | 59
Tie Node (TR_A side) | 59
Tie Node (TR_B side) | 12
Tie Line Distance (m) | 3.5
Load Transferred (kW) | 0.38
TR_A Loading After (%) | 19.6
TR_B Loading After (%) | 19.5
Minimum Voltage (V) | 221.1