## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 30 | 21 | 40 | 56 | 3 | 8.67 | 50 | 83.5 | 29.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 30 | 18 | 3 | 35 | 38.4 | 12.97 | 50 | 83.5 | 29.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 21 | 22 | 22 | 56 | 40.8 | 8.4 | 50 | 83.5 | 29.4 | 51 | 36.4 | 219.1 | 196.9 | 196.9 | NO
| NG | 18 | 17 | 3 | 35 | 38.4 | 12.43 | 50 | 83.5 | 29.4 | 35.6 | 37.8 | 219.5 | 194.5 | 194.5 | NO
| NG | 22 | 35 | 35 | 56 | 43.7 | 8.4 | 50 | 83.5 | 29.4 | 51 | 36.4 | 219.1 | 196.9 | 196.9 | NO
1 | ** OPTIMAL ** | 17 | 5 | 3 | 35 | 38.4 | 1.92 | 50 | 83.5 | 29.4 | 76.1 | 30.8 | 217.5 | 217.8 | 217.5 | YES
| NG | 17 | 20 | 20 | 56 | 95.2 | 8.28 | 50 | 83.5 | 29.4 | 51.5 | 36 | 219.5 | 206 | 206 | NO
2 | OK | 17 | 2 | 2 | 56 | 105.7 | 2.23 | 50 | 83.5 | 29.4 | 74.9 | 31.1 | 217.5 | 217.1 | 217.1 | YES
| NG | 35 | 46 | 46 | 56 | 56.4 | 8.4 | 50 | 83.5 | 29.4 | 51 | 36.4 | 219.1 | 196.7 | 196.7 | NO
| NG | 20 | 19 | 19 | 56 | 98.5 | 8.28 | 50 | 83.5 | 29.4 | 51.5 | 35.7 | 219.5 | 206.9 | 206.9 | NO
3 | OK | 2 | 1 | 6 | 48 | 117.3 | 1.82 | 50 | 83.5 | 29.4 | 76.5 | 30.8 | 217.5 | 216 | 216 | YES
| NG | 46 | 36 | 36 | 56 | 59 | 8.4 | 50 | 83.5 | 29.4 | 51 | 36.4 | 219.1 | 196.7 | 196.7 | NO
| NG | 19 | 38 | 38 | 56 | 129.6 | 7.99 | 50 | 83.5 | 29.4 | 52.6 | 35.7 | 219.5 | 206.7 | 206.7 | NO
4 | OK | 1 | 0 | 6 | 48 | 117.3 | 1.59 | 50 | 83.5 | 29.4 | 77.4 | 30.6 | 217.5 | 216.5 | 216.5 | YES
| NG | 36 | 25 | 25 | 56 | 85.3 | 5.6 | 50 | 83.5 | 29.4 | 61.8 | 33.9 | 219.1 | 206 | 206 | NO
5 | OK | 36 | 47 | 47 | 56 | 126 | 2.8 | 50 | 83.5 | 29.4 | 72.6 | 31.5 | 219.1 | 212.1 | 212.1 | YES
| NG | 38 | 37 | 37 | 56 | 150.4 | 7.7 | 50 | 83.5 | 29.4 | 53.7 | 35.5 | 219.3 | 206.4 | 206.4 | NO
| NG | 25 | 26 | 26 | 56 | 126.4 | 5.59 | 50 | 83.5 | 29.4 | 61.8 | 33.9 | 219.1 | 205.7 | 205.7 | NO
6 | OK | 47 | 45 | 45 | 56 | 167.1 | 2.58 | 50 | 83.5 | 29.4 | 73.5 | 31.4 | 219.1 | 212.8 | 212.8 | YES
| NG | 37 | 16 | 16 | 56 | 158.3 | 5.56 | 50 | 83.5 | 29.4 | 53.7 | 33.9 | 219.3 | 204.8 | 204.8 | NO
| NG | 26 | 27 | 27 | 56 | 166.6 | 4.94 | 50 | 83.5 | 29.4 | 64.3 | 33.3 | 219.1 | 207.3 | 207.3 | NO
7 | OK | 45 | 41 | 41 | 56 | 186.4 | 2.02 | 50 | 83.5 | 29.4 | 75.6 | 30.9 | 219.1 | 214.5 | 214.5 | YES
| NG | 16 | 8 | 8 | 56 | 164.8 | 5.56 | 50 | 83.5 | 29.4 | 61.9 | 33.9 | 217.6 | 204.8 | 204.8 | NO
8 | OK | 27 | 28 | 28 | 56 | 207.6 | 3.92 | 50 | 83.5 | 29.4 | 68.2 | 32.5 | 219.1 | 210.2 | 210.2 | YES
9 | OK | 41 | 42 | 42 | 56 | 199.4 | 1.63 | 50 | 83.5 | 29.4 | 77.1 | 30.6 | 219.1 | 215.6 | 215.6 | YES
| NG | 8 | 34 | 34 | 56 | 198 | 4.72 | 50 | 83.5 | 29.4 | 65.1 | 33.2 | 217.6 | 207.4 | 207.4 | NO
10 | OK | 28 | 29 | 29 | 56 | 211.9 | 2.97 | 50 | 83.5 | 29.4 | 71.9 | 31.7 | 219.1 | 213.5 | 213.5 | YES
11 | OK | 34 | 15 | 15 | 56 | 224.1 | 3.31 | 50 | 83.5 | 29.4 | 70.6 | 32 | 217.7 | 212.2 | 212.2 | YES
12 | OK | 15 | 9 | 9 | 56 | 227.6 | 1.11 | 50 | 83.5 | 29.4 | 79.1 | 30.2 | 217.5 | 218.9 | 217.5 | YES
13 | OK | 15 | 31 | 31 | 56 | 227.2 | 2.2 | 50 | 83.5 | 29.4 | 74.9 | 31.1 | 217.7 | 216 | 216 | YES
| NG | 31 | 14 | 56 | 56 | 238.7 | 2.2 | 50 | 83.5 | 29.4 | 74.9 | 11953.4 | 217.7 | 109.9 | 109.9 | NO
14 | OK | 14 | 13 | 56 | 56 | 238.7 | 2.2 | 50 | 83.5 | 29.4 | 74.9 | 31.1 | 217.7 | 215.9 | 215.9 | YES
15 | OK | 13 | 33 | 56 | 56 | 238.7 | 2.2 | 50 | 83.5 | 29.4 | 74.9 | 30.9 | 217.7 | 216 | 216 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 51-013851
TR_B (available) | 28-001040
TR_A Rated kVA | 30
TR_B Rated kVA | 160
TR_A Baseline Loading% | 83.5
TR_B Baseline Loading% | 29.4
Total Scenarios Evaluated | 33
Feasible Scenarios | 15
--- Optimal Solution ---
Switch Parent Node | 17
Switch Child Node | 5
Tie Node (TR_A side) | 3
Tie Node (TR_B side) | 35
Tie Line Distance (m) | 38.4
Load Transferred (kW) | 1.92
TR_A Loading After (%) | 76.1
TR_B Loading After (%) | 30.8
Minimum Voltage (V) | 217.5