## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 18 | 17 | 11 | 11 | 148.6 | 12.43 | 50 | 83.5 | 37 | 35.6 | 47.2 | 219.5 | 215.6 | 215.6 | YES
2 | OK | 17 | 20 | 11 | 11 | 148.6 | 8.28 | 50 | 83.5 | 37 | 51.5 | 47.2 | 219.5 | 215.6 | 215.6 | YES
3 | OK | 20 | 19 | 11 | 11 | 148.6 | 8.28 | 50 | 83.5 | 37 | 51.5 | 47.2 | 219.5 | 215.6 | 215.6 | YES
4 | OK | 19 | 38 | 11 | 11 | 148.6 | 7.99 | 50 | 83.5 | 37 | 52.6 | 47.2 | 219.5 | 215.6 | 215.6 | YES
5 | OK | 38 | 37 | 11 | 11 | 148.6 | 7.7 | 50 | 83.5 | 37 | 53.7 | 46 | 219.3 | 216.3 | 216.3 | YES
6 | ** OPTIMAL ** | 37 | 16 | 11 | 11 | 148.6 | 5.56 | 50 | 83.5 | 37 | 53.7 | 37.5 | 219.3 | 220.8 | 219.3 | YES
7 | OK | 16 | 8 | 11 | 11 | 148.6 | 5.56 | 50 | 83.5 | 37 | 61.9 | 37.5 | 217.6 | 220.8 | 217.6 | YES
8 | OK | 8 | 34 | 11 | 11 | 148.6 | 4.72 | 50 | 83.5 | 37 | 65.1 | 37.5 | 217.6 | 220.8 | 217.6 | YES
9 | OK | 34 | 15 | 11 | 11 | 148.6 | 3.31 | 50 | 83.5 | 37 | 70.6 | 37.5 | 217.7 | 220.8 | 217.7 | YES
10 | OK | 15 | 9 | 10 | 11 | 221 | 1.11 | 50 | 83.5 | 37 | 79.1 | 41.3 | 217.5 | 219.1 | 217.5 | YES
11 | OK | 15 | 31 | 11 | 11 | 148.6 | 2.2 | 50 | 83.5 | 37 | 74.9 | 37.5 | 217.7 | 220.8 | 217.7 | YES
| NG | 31 | 14 | 11 | 11 | 148.6 | 2.2 | 50 | 83.5 | 37 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 37.0% (degenerate)
12 | OK | 14 | 13 | 11 | 11 | 148.6 | 2.2 | 50 | 83.5 | 37 | 74.9 | 37.5 | 217.7 | 220.8 | 217.7 | YES
13 | OK | 13 | 33 | 11 | 11 | 148.6 | 2.2 | 50 | 83.5 | 37 | 74.9 | 37 | 217.7 | 220.9 | 217.7 | YES
14 | OK | 33 | 32 | 11 | 11 | 148.6 | 1.06 | 50 | 83.5 | 37 | 79.3 | 37 | 217.5 | 220.9 | 217.5 | YES
15 | OK | 32 | 12 | 11 | 11 | 148.6 | 1.06 | 50 | 83.5 | 37 | 79.3 | 37 | 217.5 | 220.9 | 217.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 51-013851
TR_B (available) | 47-002493
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 83.5
TR_B Baseline Loading% | 37
Total Scenarios Evaluated | 16
Feasible Scenarios | 15
--- Optimal Solution ---
Switch Parent Node | 37
Switch Child Node | 16
Tie Node (TR_A side) | 11
Tie Node (TR_B side) | 11
Tie Line Distance (m) | 148.6
Load Transferred (kW) | 5.56
TR_A Loading After (%) | 53.7
TR_B Loading After (%) | 37.5
Minimum Voltage (V) | 219.3