## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 30 | 21 | 24 | 42 | 3.1 | 8.67 | 50 | 83.5 | 29.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 21 | 22 | 24 | 42 | 3.1 | 8.4 | 50 | 83.5 | 29.6 | [5 empty] | NO | TR_B sim: not converged
| NG | 22 | 35 | 24 | 42 | 3.1 | 8.4 | 50 | 83.5 | 29.6 | [5 empty] | NO | TR_B sim: not converged
| NG | 35 | 46 | 24 | 42 | 3.1 | 8.4 | 50 | 83.5 | 29.6 | [5 empty] | NO | TR_B sim: not converged
| NG | 46 | 36 | 24 | 42 | 3.1 | 8.4 | 50 | 83.5 | 29.6 | [5 empty] | NO | TR_B sim: not converged
| NG | 36 | 47 | 24 | 42 | 3.1 | 2.8 | 50 | 83.5 | 29.6 | 72.6 | 42.1 | 219.1 | 198.1 | 198.1 | NO
| NG | 47 | 45 | 24 | 42 | 3.1 | 2.58 | 50 | 83.5 | 29.6 | 73.5 | 41.1 | 219.1 | 199.8 | 199.8 | NO
| NG | 45 | 41 | 24 | 42 | 3.1 | 2.02 | 50 | 83.5 | 29.6 | 75.6 | 38.4 | 219.1 | 204.1 | 204.1 | NO
| NG | 41 | 42 | 24 | 42 | 3.1 | 1.63 | 50 | 83.5 | 29.6 | 77.1 | 36.6 | 219.1 | 206.9 | 206.9 | NO
| NG | 42 | 50 | 24 | 42 | 3.1 | 1.52 | 50 | 83.5 | 29.6 | 77.6 | 36.1 | 219.1 | 207.7 | 207.7 | NO
| NG | 50 | 43 | 24 | 42 | 3.1 | 1.52 | 50 | 83.5 | 29.6 | 77.6 | 36.1 | 219.1 | 207.7 | 207.7 | NO
1 | ** OPTIMAL ** | 43 | 44 | 24 | 42 | 3.1 | 1.09 | 50 | 83.5 | 29.6 | 79.2 | 34.2 | 219.1 | 210.4 | 210.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 51-013851
TR_B (available) | 56-004014
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 83.5
TR_B Baseline Loading% | 29.6
Total Scenarios Evaluated | 12
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 43
Switch Child Node | 44
Tie Node (TR_A side) | 24
Tie Node (TR_B side) | 42
Tie Line Distance (m) | 3.1
Load Transferred (kW) | 1.09
TR_A Loading After (%) | 79.2
TR_B Loading After (%) | 34.2
Minimum Voltage (V) | 210.4