## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 43 | 18 | 11 | 38 | 23.9 | 16.86 | 50 | 88.6 | 36.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 18 | 19 | 11 | 38 | 23.9 | 15.75 | 50 | 88.6 | 36.9 | 51.9 | 56.2 | 218.7 | 210.8 | 210.8 | YES
2 | OK | 19 | 57 | 11 | 38 | 23.9 | 14.87 | 50 | 88.6 | 36.9 | 53.9 | 54.8 | 218.4 | 210.7 | 210.7 | YES
3 | OK | 57 | 59 | 11 | 38 | 23.9 | 14.66 | 50 | 88.6 | 36.9 | 54.4 | 54.8 | 218.3 | 210.7 | 210.7 | YES
4 | OK | 59 | 17 | 11 | 38 | 23.9 | 13.71 | 50 | 88.6 | 36.9 | 54.7 | 53.7 | 218.3 | 210.6 | 210.6 | YES
5 | OK | 17 | 0 | 11 | 38 | 23.9 | 13.03 | 50 | 88.6 | 36.9 | 58.1 | 52.9 | 217.8 | 210.4 | 210.4 | YES
6 | OK | 0 | 4 | 11 | 38 | 23.9 | 11.52 | 50 | 88.6 | 36.9 | 61.6 | 50.9 | 217.8 | 212.6 | 212.6 | YES
7 | OK | 4 | 9 | 11 | 38 | 23.9 | 9.44 | 50 | 88.6 | 36.9 | 66.4 | 48.3 | 217.7 | 215 | 215 | YES
8 | OK | 9 | 10 | 11 | 38 | 23.9 | 8.69 | 50 | 88.6 | 36.9 | 66.4 | 47.4 | 217.7 | 215 | 215 | YES
9 | OK | 10 | 11 | 11 | 38 | 23.9 | 8.62 | 50 | 88.6 | 36.9 | 68.3 | 47.3 | 217.3 | 215.1 | 215.1 | YES
10 | OK | 11 | 12 | 12 | 38 | 25.3 | 8.62 | 50 | 88.6 | 36.9 | 68.3 | 47.3 | 217.3 | 215.1 | 215.1 | YES
11 | ** OPTIMAL ** | 12 | 13 | 13 | 39 | 29.9 | 7.76 | 50 | 88.6 | 36.9 | 70.3 | 46.3 | 217.3 | 215.7 | 215.7 | YES
| NG | 13 | 14 | 51 | 18 | 33.8 | 7.76 | 50 | 88.6 | 36.9 | 70.3 | 47.8 | 217.3 | 194 | 194 | NO
| NG | 14 | 15 | 51 | 18 | 33.8 | 7.49 | 50 | 88.6 | 36.9 | 71 | 47.3 | 217.2 | 195 | 195 | NO
| NG | 15 | 16 | 51 | 18 | 33.8 | 6.04 | 50 | 88.6 | 36.9 | 74.3 | 45.1 | 216.9 | 200 | 200 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 52-000133
TR_B (available) | 31-005079
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 88.6
TR_B Baseline Loading% | 36.9
Total Scenarios Evaluated | 15
Feasible Scenarios | 11
--- Optimal Solution ---
Switch Parent Node | 12
Switch Child Node | 13
Tie Node (TR_A side) | 13
Tie Node (TR_B side) | 39
Tie Line Distance (m) | 29.9
Load Transferred (kW) | 7.76
TR_A Loading After (%) | 70.3
TR_B Loading After (%) | 46.3
Minimum Voltage (V) | 215.7