## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 43 | 18 | 44 | 39 | 4 | 16.86 | 50 | 88.6 | 41.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 43 | 21 | 30 | 13 | 43 | 21.25 | 50 | 88.6 | 41.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 18 | 19 | 44 | 39 | 4 | 15.75 | 50 | 88.6 | 41.9 | 51.9 | 61.4 | 218.7 | 209.1 | 209.1 | NO
| NG | 21 | 20 | 30 | 13 | 43 | 20.91 | 50 | 88.6 | 41.9 | 40 | 70.6 | 221.5 | 176.1 | 176.1 | NO
| NG | 19 | 57 | 44 | 39 | 4 | 14.87 | 50 | 88.6 | 41.9 | 53.9 | 60.1 | 218.4 | 208.9 | 208.9 | NO
| NG | 20 | 58 | 30 | 13 | 43 | 19.87 | 50 | 88.6 | 41.9 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 41.9% (degenerate)
| NG | 57 | 59 | 44 | 39 | 4 | 14.66 | 50 | 88.6 | 41.9 | 54.4 | 60.1 | 218.3 | 208.9 | 208.9 | NO
| NG | 58 | 24 | 30 | 13 | 43 | 18.58 | 50 | 88.6 | 41.9 | 45.3 | 66.9 | 221.1 | 181.9 | 181.9 | NO
| NG | 59 | 17 | 44 | 39 | 4 | 13.71 | 50 | 88.6 | 41.9 | 54.7 | 58.9 | 218.3 | 208.7 | 208.7 | NO
| NG | 24 | 23 | 30 | 13 | 43 | 10.07 | 50 | 88.6 | 41.9 | 65 | 54.2 | 218.3 | 207.5 | 207.5 | NO
| NG | 17 | 0 | 44 | 39 | 4 | 13.03 | 50 | 88.6 | 41.9 | 58.1 | 58.1 | 217.8 | 208.6 | 208.6 | NO
| NG | 23 | 22 | 30 | 13 | 43 | 10.03 | 50 | 88.6 | 41.9 | 65.1 | 54.1 | 218.3 | 207.6 | 207.6 | NO
1 | OK | 0 | 4 | 44 | 39 | 4 | 11.52 | 50 | 88.6 | 41.9 | 61.6 | 56.1 | 217.8 | 211.4 | 211.4 | YES
2 | OK | 4 | 9 | 9 | 39 | 50.7 | 9.44 | 50 | 88.6 | 41.9 | 66.4 | 53.5 | 217.7 | 214.3 | 214.3 | YES
3 | OK | 9 | 10 | 10 | 39 | 60.6 | 8.69 | 50 | 88.6 | 41.9 | 66.4 | 52.5 | 217.7 | 214.2 | 214.2 | YES
4 | OK | 10 | 11 | 11 | 39 | 79.1 | 8.62 | 50 | 88.6 | 41.9 | 68.3 | 52.5 | 217.3 | 214.3 | 214.3 | YES
5 | OK | 11 | 12 | 12 | 39 | 88.3 | 8.62 | 50 | 88.6 | 41.9 | 68.3 | 52.5 | 217.3 | 214.3 | 214.3 | YES
6 | ** OPTIMAL ** | 12 | 13 | 13 | 39 | 141.5 | 7.76 | 50 | 88.6 | 41.9 | 70.3 | 51.4 | 217.3 | 216 | 216 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 52-000133
TR_B (available) | 52-940029
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 88.6
TR_B Baseline Loading% | 41.9
Total Scenarios Evaluated | 18
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 12
Switch Child Node | 13
Tie Node (TR_A side) | 13
Tie Node (TR_B side) | 39
Tie Line Distance (m) | 141.5
Load Transferred (kW) | 7.76
TR_A Loading After (%) | 70.3
TR_B Loading After (%) | 51.4
Minimum Voltage (V) | 216