## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 16 | 64 | 18 | 23 | 76.4 | 3.73 | 50 | 77.7 | 51.3 | 69 | 61.1 | 216.9 | 207.3 | 207.3 | NO
| NG | 64 | 56 | 18 | 23 | 76.4 | 3.49 | 50 | 77.7 | 51.3 | 69.5 | 61.1 | 216.9 | 207.3 | 207.3 | NO
| NG | 56 | 42 | 18 | 23 | 76.4 | 2.86 | 50 | 77.7 | 51.3 | 71 | 58.5 | 216.9 | 209.6 | 209.6 | NO
1 | OK | 42 | 43 | 18 | 23 | 76.4 | 1.32 | 50 | 77.7 | 51.3 | 74.6 | 52.9 | 216.8 | 212.9 | 212.9 | YES
2 | ** OPTIMAL ** | 43 | 19 | 18 | 23 | 76.4 | 0.73 | 50 | 77.7 | 51.3 | 76 | 52.8 | 216.8 | 213 | 213 | YES
3 | OK | 19 | 18 | 18 | 23 | 76.4 | 0.73 | 50 | 77.7 | 51.3 | 76 | 52.8 | 216.8 | 213 | 213 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 52-001530
TR_B (available) | 42-006048
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 77.7
TR_B Baseline Loading% | 51.3
Total Scenarios Evaluated | 6
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 43
Switch Child Node | 19
Tie Node (TR_A side) | 18
Tie Node (TR_B side) | 23
Tie Line Distance (m) | 76.4
Load Transferred (kW) | 0.73
TR_A Loading After (%) | 76
TR_B Loading After (%) | 52.8
Minimum Voltage (V) | 213