## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 8 | 6 | 10 | 8 | 24.5 | 12.8 | 50 | 77.7 | 45.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 8 | 25 | 39 | 88 | 24.1 | 20.68 | 50 | 77.7 | 45.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 6 | 7 | 10 | 8 | 24.5 | 11.73 | 50 | 77.7 | 45.6 | 50.4 | 51.9 | 221 | 198.5 | 198.5 | NO
| NG | 25 | 26 | 39 | 88 | 24.1 | 20.14 | 50 | 77.7 | 45.6 | 31 | 55.3 | 219.7 | 187.9 | 187.9 | NO
| NG | 7 | 9 | 10 | 8 | 24.5 | 11.21 | 50 | 77.7 | 45.6 | 51.6 | 51.9 | 221 | 198.5 | 198.5 | NO
| NG | 26 | 22 | 39 | 88 | 24.1 | 20.14 | 50 | 77.7 | 45.6 | 31 | 55.3 | 219.7 | 187.9 | 187.9 | NO
| NG | 9 | 55 | 10 | 8 | 24.5 | 11.21 | 50 | 77.7 | 45.6 | 51.6 | 51.9 | 221 | 198.5 | 198.5 | NO
| NG | 22 | 23 | 39 | 88 | 24.1 | 18.76 | 50 | 77.7 | 45.6 | 34.1 | 55.3 | 219.7 | 187.9 | 187.9 | NO
| NG | 55 | 66 | 10 | 8 | 24.5 | 9.87 | 50 | 77.7 | 45.6 | 54.7 | 49.9 | 221 | 202.2 | 202.2 | NO
| NG | 23 | 24 | 39 | 88 | 24.1 | 6.17 | 50 | 77.7 | 45.6 | 63.4 | 49.3 | 218 | 208.1 | 208.1 | NO
| NG | 66 | 28 | 10 | 8 | 24.5 | 8.68 | 50 | 77.7 | 45.6 | 56.3 | 49.6 | 220.7 | 202.8 | 202.8 | NO
| NG | 24 | 35 | 39 | 88 | 24.1 | 5.8 | 50 | 77.7 | 45.6 | 64.2 | 49.3 | 217.8 | 208.1 | 208.1 | NO
| NG | 28 | 27 | 10 | 8 | 24.5 | 8.68 | 50 | 77.7 | 45.6 | 57.4 | 49.6 | 220.7 | 202.8 | 202.8 | NO
| NG | 35 | 65 | 39 | 88 | 24.1 | 5.66 | 50 | 77.7 | 45.6 | 64.5 | 49.3 | 217.7 | 208.1 | 208.1 | NO
| NG | 27 | 62 | 10 | 8 | 24.5 | 8.27 | 50 | 77.7 | 45.6 | 58.4 | 49 | 220.7 | 203.9 | 203.9 | NO
| NG | 65 | 31 | 39 | 88 | 24.1 | 5.5 | 50 | 77.7 | 45.6 | 64.9 | 49.3 | 217.6 | 208.1 | 208.1 | NO
| NG | 62 | 61 | 10 | 8 | 24.5 | 6.7 | 50 | 77.7 | 45.6 | 62 | 48.4 | 220.1 | 205.1 | 205.1 | NO
| NG | 31 | 32 | 39 | 88 | 24.1 | 4.57 | 50 | 77.7 | 45.6 | 67.1 | 48 | 217.6 | 208.9 | 208.9 | NO
| NG | 61 | 63 | 10 | 8 | 24.5 | 5.47 | 50 | 77.7 | 45.6 | 64.8 | 48.4 | 220.2 | 205.1 | 205.1 | NO
| NG | 32 | 36 | 39 | 88 | 24.1 | 3.69 | 50 | 77.7 | 45.6 | 69.1 | 46.9 | 217.6 | 209.6 | 209.6 | NO
| NG | 63 | 41 | 10 | 8 | 24.5 | 4.55 | 50 | 77.7 | 45.6 | 66.9 | 47.2 | 220.2 | 207.5 | 207.5 | NO
| NG | 36 | 37 | 39 | 88 | 24.1 | 3.06 | 50 | 77.7 | 45.6 | 70.6 | 46.8 | 217.4 | 209.7 | 209.7 | NO
| NG | 41 | 40 | 10 | 8 | 24.5 | 4.4 | 50 | 77.7 | 45.6 | 67.3 | 46.8 | 220.2 | 208.2 | 208.2 | NO
| NG | 37 | 29 | 39 | 88 | 24.1 | 1.48 | 50 | 77.7 | 45.6 | 74.2 | 46.8 | 217 | 209.7 | 209.7 | NO
| NG | 40 | 11 | 10 | 8 | 24.5 | 0.94 | 50 | 77.7 | 45.6 | 75.5 | 46.8 | 216.3 | 208.2 | 208.2 | NO
| NG | 40 | 45 | 45 | 8 | 84.8 | 3.16 | 50 | 77.7 | 45.6 | 70.2 | 49.8 | 220.2 | 202.5 | 202.5 | NO
| NG | 29 | 30 | 39 | 88 | 24.1 | 0.96 | 50 | 77.7 | 45.6 | 75.5 | 46.8 | 216.7 | 209.7 | 209.7 | NO
1 | ** OPTIMAL ** | 45 | 46 | 52 | 16 | 89.2 | 2.19 | 50 | 77.7 | 45.6 | 72.5 | 48.3 | 220.2 | 210.7 | 210.7 | YES
| NG | 30 | 44 | 44 | 37 | 53.6 | 0.96 | 50 | 77.7 | 45.6 | 75.5 | 46.8 | 216.7 | 209.7 | 209.7 | NO
2 | OK | 46 | 49 | 52 | 16 | 89.2 | 1.35 | 50 | 77.7 | 45.6 | 74.4 | 47.2 | 220.2 | 210.6 | 210.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 52-001530
TR_B (available) | 58-015525
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 77.7
TR_B Baseline Loading% | 45.6
Total Scenarios Evaluated | 30
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 45
Switch Child Node | 46
Tie Node (TR_A side) | 52
Tie Node (TR_B side) | 16
Tie Line Distance (m) | 89.2
Load Transferred (kW) | 2.19
TR_A Loading After (%) | 72.5
TR_B Loading After (%) | 48.3
Minimum Voltage (V) | 210.7