## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 43 | 42 | 36 | 190 | 144.2 | 12.3 | 50 | 50 | 40.4 | 21.6 | 43.7 | 225.4 | 210.5 | 210.5 | YES
2 | OK | 42 | 41 | 36 | 190 | 144.2 | 9.41 | 50 | 50 | 40.4 | 28.2 | 43.7 | 224.1 | 210.5 | 210.5 | YES
3 | OK | 41 | 40 | 36 | 190 | 144.2 | 8.17 | 50 | 50 | 40.4 | 31.1 | 43.7 | 224.1 | 210.5 | 210.5 | YES
4 | ** OPTIMAL ** | 40 | 48 | 36 | 190 | 144.2 | 5.95 | 50 | 50 | 40.4 | 36.2 | 41.9 | 224.1 | 217.7 | 217.7 | YES
5 | OK | 48 | 47 | 36 | 190 | 144.2 | 4.5 | 50 | 50 | 40.4 | 39.5 | 41.7 | 223.8 | 217.7 | 217.7 | YES
6 | OK | 47 | 39 | 36 | 190 | 144.2 | 1.88 | 50 | 50 | 40.4 | 45.6 | 41.7 | 222.2 | 217.7 | 217.7 | YES
7 | OK | 39 | 46 | 36 | 190 | 144.2 | 1.83 | 50 | 50 | 40.4 | 45.7 | 41.7 | 222.2 | 217.7 | 217.7 | YES
8 | OK | 46 | 36 | 36 | 190 | 144.2 | 1.29 | 50 | 50 | 40.4 | 47 | 41.3 | 222.2 | 217.7 | 217.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 52-001594
TR_B (available) | 54-003745
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 50
TR_B Baseline Loading% | 40.4
Total Scenarios Evaluated | 8
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 40
Switch Child Node | 48
Tie Node (TR_A side) | 36
Tie Node (TR_B side) | 190
Tie Line Distance (m) | 144.2
Load Transferred (kW) | 5.95
TR_A Loading After (%) | 36.2
TR_B Loading After (%) | 41.9
Minimum Voltage (V) | 217.7