## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 16 | 22 | 26 | 29 | 176.6 | 10.37 | 50 | 94.1 | 21 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 22 | 21 | 26 | 29 | 176.6 | 10.37 | 50 | 94.1 | 21 | 54.3 | 22.8 | 215.3 | 223.7 | 215.3 | YES
2 | ** OPTIMAL ** | 21 | 4 | 26 | 29 | 176.6 | 10.37 | 50 | 94.1 | 21 | 54.3 | 22.8 | 215.3 | 223.7 | 215.3 | YES
3 | OK | 4 | 3 | 26 | 29 | 176.6 | 5.92 | 50 | 94.1 | 21 | 67.9 | 21.1 | 214.2 | 223.6 | 214.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 52-009882
TR_B (available) | 65-018355
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 94.1
TR_B Baseline Loading% | 21
Total Scenarios Evaluated | 4
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 21
Switch Child Node | 4
Tie Node (TR_A side) | 26
Tie Node (TR_B side) | 29
Tie Line Distance (m) | 176.6
Load Transferred (kW) | 10.37
TR_A Loading After (%) | 54.3
TR_B Loading After (%) | 22.8
Minimum Voltage (V) | 215.3