## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 0 | 20 | 30 | 82 | 2.9 | 3.25 | 50 | 18.1 | 29.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 20 | 26 | 30 | 82 | 2.9 | 2.82 | 50 | 18.1 | 29.9 | 11.7 | 32.5 | 227.4 | 209.9 | 209.9 | NO
| NG | 26 | 25 | 30 | 82 | 2.9 | 2.82 | 50 | 18.1 | 29.9 | 11.7 | 32.5 | 227.4 | 209.9 | 209.9 | NO
| NG | 25 | 32 | 30 | 82 | 2.9 | 2.82 | 50 | 18.1 | 29.9 | 11.7 | 32.5 | 227.4 | 209.9 | 209.9 | NO
1 | OK | 32 | 22 | 30 | 82 | 2.9 | 2.73 | 50 | 18.1 | 29.9 | 11.9 | 32.3 | 227.4 | 210.1 | 210.1 | YES
2 | OK | 22 | 21 | 30 | 82 | 2.9 | 2.71 | 50 | 18.1 | 29.9 | 11.9 | 32.3 | 227.4 | 210.1 | 210.1 | YES
3 | OK | 21 | 31 | 30 | 82 | 2.9 | 2.33 | 50 | 18.1 | 29.9 | 12.8 | 32.2 | 227.3 | 210.2 | 210.2 | YES
4 | OK | 31 | 24 | 30 | 82 | 2.9 | 1.8 | 50 | 18.1 | 29.9 | 12.8 | 32.2 | 227.3 | 210.2 | 210.2 | YES
5 | OK | 24 | 23 | 30 | 82 | 2.9 | 1.8 | 50 | 18.1 | 29.9 | 14 | 32.1 | 227 | 210.4 | 210.4 | YES
6 | OK | 23 | 19 | 30 | 82 | 2.9 | 1.7 | 50 | 18.1 | 29.9 | 14.2 | 32.1 | 227 | 210.4 | 210.4 | YES
7 | OK | 19 | 27 | 30 | 82 | 2.9 | 1.7 | 50 | 18.1 | 29.9 | 14.2 | 32.1 | 227 | 210.4 | 210.4 | YES
8 | OK | 27 | 28 | 30 | 82 | 2.9 | 1.7 | 50 | 18.1 | 29.9 | 14.2 | 32.1 | 227 | 210.4 | 210.4 | YES
9 | ** OPTIMAL ** | 28 | 29 | 30 | 82 | 2.9 | 0.44 | 50 | 18.1 | 29.9 | 17.1 | 30.4 | 227 | 212.6 | 212.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 52-930244
TR_B (available) | 60-025800
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 18.1
TR_B Baseline Loading% | 29.9
Total Scenarios Evaluated | 13
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 28
Switch Child Node | 29
Tie Node (TR_A side) | 30
Tie Node (TR_B side) | 82
Tie Line Distance (m) | 2.9
Load Transferred (kW) | 0.44
TR_A Loading After (%) | 17.1
TR_B Loading After (%) | 30.4
Minimum Voltage (V) | 212.6