## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 0 | 1 | 17 | 81 | 2 | 4.64 | 50 | 18.1 | 26.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 1 | 9 | 17 | 81 | 2 | 4.28 | 50 | 18.1 | 26.8 | 8.3 | 28.8 | 227.9 | 220.7 | 220.7 | YES
2 | OK | 9 | 10 | 17 | 81 | 2 | 3.84 | 50 | 18.1 | 26.8 | 9.3 | 28.6 | 227.9 | 220.7 | 220.7 | YES
3 | ** OPTIMAL ** | 10 | 14 | 17 | 81 | 2 | 3.61 | 50 | 18.1 | 26.8 | 9.8 | 28.5 | 227.8 | 220.8 | 220.8 | YES
4 | OK | 14 | 15 | 17 | 81 | 2 | 3.61 | 50 | 18.1 | 26.8 | 9.8 | 28.5 | 227.8 | 220.8 | 220.8 | YES
5 | OK | 15 | 2 | 17 | 81 | 2 | 3.61 | 50 | 18.1 | 26.8 | 9.8 | 28.5 | 227.8 | 220.8 | 220.8 | YES
6 | OK | 2 | 3 | 17 | 81 | 2 | 3.33 | 50 | 18.1 | 26.8 | 10.5 | 28.4 | 227.8 | 220.8 | 220.8 | YES
7 | OK | 3 | 18 | 17 | 81 | 2 | 0.53 | 50 | 18.1 | 26.8 | 16.9 | 27.1 | 227.1 | 220.6 | 220.6 | YES
8 | OK | 18 | 16 | 17 | 81 | 2 | 0.19 | 50 | 18.1 | 26.8 | 17.7 | 26.9 | 227.2 | 220.8 | 220.8 | YES
9 | OK | 16 | 17 | 17 | 81 | 2 | 0.19 | 50 | 18.1 | 26.8 | 17.7 | 26.9 | 227.2 | 220.8 | 220.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 52-930244
TR_B (available) | 60-037021
TR_A Rated kVA | 50
TR_B Rated kVA | 250
TR_A Baseline Loading% | 18.1
TR_B Baseline Loading% | 26.8
Total Scenarios Evaluated | 10
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 10
Switch Child Node | 14
Tie Node (TR_A side) | 17
Tie Node (TR_B side) | 81
Tie Line Distance (m) | 2
Load Transferred (kW) | 3.61
TR_A Loading After (%) | 9.8
TR_B Loading After (%) | 28.5
Minimum Voltage (V) | 220.8