## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 5 | 7 | 7 | 47 | 113.3 | 26.02 | 50 | 85.8 | 62.8 | 66.7 | 75.9 | 181.4 | 176.6 | 176.6 | NO
| NG | 7 | 29 | 29 | 47 | 132 | 24.59 | 50 | 85.8 | 62.8 | 67.7 | 74.4 | 181.4 | 179.9 | 179.9 | NO
| NG | 29 | 1 | 1 | 47 | 137.8 | 24.21 | 50 | 85.8 | 62.8 | 68 | 74 | 181.4 | 180.9 | 180.9 | NO
| NG | 9 | 40 | 40 | 47 | 81 | 23.64 | 50 | 85.8 | 62.8 | 68.2 | 74.3 | 181.1 | 188.3 | 181.1 | NO
| NG | 1 | 0 | 0 | 47 | 148.3 | 23.46 | 50 | 85.8 | 62.8 | 68.5 | 74 | 181.3 | 180.9 | 180.9 | NO
| NG | 40 | 41 | 43 | 47 | 90.9 | 23.64 | 50 | 85.8 | 62.8 | 68.2 | 74.3 | 181.1 | 189 | 181.1 | NO
| NG | 11 | 103 | 28 | 31 | 2.5 | 10.06 | 50 | 85.8 | 62.8 | 78.1 | 69.4 | 180.5 | 206.8 | 180.5 | NO
| NG | 41 | 42 | 42 | 47 | 122.4 | 13.9 | 50 | 85.8 | 62.8 | 75.4 | 66.3 | 181.6 | 205 | 181.6 | NO
| NG | 103 | 102 | 28 | 31 | 2.5 | 9.56 | 50 | 85.8 | 62.8 | 78.5 | 69.1 | 180.2 | 206.8 | 180.2 | NO
| NG | 42 | 54 | 54 | 47 | 149.1 | 13.56 | 50 | 85.8 | 62.8 | 75.6 | 66.3 | 181.6 | 205 | 181.6 | NO
1 | ** OPTIMAL ** | 57 | 70 | 70 | 47 | 133.7 | 27.14 | 50 | 85.8 | 62.8 | 62.7 | 62.9 | 211.7 | 212.8 | 211.7 | YES
2 | OK | 70 | 71 | 71 | 47 | 137.5 | 25.98 | 50 | 85.8 | 62.8 | 63.6 | 62.9 | 210.3 | 212.8 | 210.3 | YES
| NG | 71 | 59 | 59 | 47 | 142.4 | 12.47 | 50 | 85.8 | 62.8 | 74.9 | 62.8 | 194.8 | 212.8 | 194.8 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 52-930250
TR_B (available) | 46-007374
TR_A Rated kVA | 160
TR_B Rated kVA | 160
TR_A Baseline Loading% | 85.8
TR_B Baseline Loading% | 62.8
Total Scenarios Evaluated | 13
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 57
Switch Child Node | 70
Tie Node (TR_A side) | 70
Tie Node (TR_B side) | 47
Tie Line Distance (m) | 133.7
Load Transferred (kW) | 27.14
TR_A Loading After (%) | 62.7
TR_B Loading After (%) | 62.9
Minimum Voltage (V) | 211.7