## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 5 | 7 | 21 | 13 | 77.2 | 26.02 | 50 | 85.8 | 47.1 | 66.7 | 63.1 | 181.4 | 197.4 | 181.4 | NO
| NG | 7 | 29 | 21 | 13 | 77.2 | 24.59 | 50 | 85.8 | 47.1 | 67.7 | 61.8 | 181.4 | 201.8 | 181.4 | NO
| NG | 29 | 1 | 21 | 13 | 77.2 | 24.21 | 50 | 85.8 | 47.1 | 68 | 60.9 | 181.4 | 202.7 | 181.4 | NO
| NG | 1 | 0 | 21 | 13 | 77.2 | 23.46 | 50 | 85.8 | 47.1 | 68.5 | 60.9 | 181.3 | 202.7 | 181.3 | NO
| NG | 0 | 98 | 21 | 13 | 77.2 | 23.08 | 50 | 85.8 | 47.1 | 68.8 | 60.7 | 181.3 | 202.7 | 181.3 | NO
| NG | 11 | 22 | 77 | 16 | 28.6 | 49.4 | 50 | 85.8 | 47.1 | 46.1 | 58.2 | 215.1 | 178 | 178 | NO
| NG | 98 | 16 | 21 | 13 | 77.2 | 22.54 | 50 | 85.8 | 47.1 | 68.8 | 60.6 | 181.3 | 202.6 | 181.3 | NO
| NG | 22 | 101 | 77 | 16 | 28.6 | 40.97 | 50 | 85.8 | 47.1 | 52.2 | 55.3 | 214.8 | 187.7 | 187.7 | NO
| NG | 16 | 2 | 21 | 13 | 77.2 | 21.25 | 50 | 85.8 | 47.1 | 70.1 | 60.1 | 181.2 | 202.5 | 181.2 | NO
| NG | 101 | 100 | 77 | 16 | 28.6 | 40.97 | 50 | 85.8 | 47.1 | 52.2 | 55.3 | 214.8 | 187.7 | 187.7 | NO
| NG | 2 | 4 | 21 | 13 | 77.2 | 13.74 | 50 | 85.8 | 47.1 | 75.5 | 57.4 | 181 | 209.3 | 181 | NO
| NG | 100 | 133 | 77 | 16 | 28.6 | 40.54 | 50 | 85.8 | 47.1 | 52.5 | 55.1 | 214.7 | 188.6 | 188.6 | NO
| NG | 4 | 38 | 21 | 13 | 77.2 | 13.34 | 50 | 85.8 | 47.1 | 75.8 | 56.7 | 181 | 211.1 | 181 | NO
| NG | 133 | 132 | 77 | 16 | 28.6 | 40.38 | 50 | 85.8 | 47.1 | 52.7 | 55.1 | 214.7 | 188.6 | 188.6 | NO
| NG | 38 | 34 | 21 | 13 | 77.2 | 12.99 | 50 | 85.8 | 47.1 | 76.1 | 56.7 | 181 | 211.1 | 181 | NO
| NG | 132 | 131 | 77 | 16 | 28.6 | 39.74 | 50 | 85.8 | 47.1 | 53.1 | 55.1 | 214.7 | 188.6 | 188.6 | NO
| NG | 34 | 33 | 21 | 13 | 77.2 | 9.72 | 50 | 85.8 | 47.1 | 78.4 | 54.1 | 181 | 213 | 181 | NO
| NG | 131 | 82 | 77 | 16 | 28.6 | 39.74 | 50 | 85.8 | 47.1 | 53 | 55.1 | 214.7 | 188.6 | 188.6 | NO
| NG | 33 | 32 | 21 | 13 | 77.2 | 9.72 | 50 | 85.8 | 47.1 | 78.4 | 54.1 | 181 | 213 | 181 | NO
| NG | 82 | 58 | 77 | 16 | 28.6 | 30.12 | 50 | 85.8 | 47.1 | 60.1 | 50.6 | 214 | 205.7 | 205.7 | NO
| NG | 82 | 90 | 87 | 13 | 112.6 | 9.62 | 50 | 85.8 | 47.1 | 78 | 54.3 | 183.3 | 213.2 | 183.3 | NO
| NG | 32 | 31 | 21 | 13 | 77.2 | 9.35 | 50 | 85.8 | 47.1 | 78.7 | 53.9 | 181 | 213 | 181 | NO
| NG | 58 | 55 | 77 | 16 | 28.6 | 29.07 | 50 | 85.8 | 47.1 | 61.1 | 49.7 | 213.9 | 208.7 | 208.7 | NO
| NG | 55 | 57 | 77 | 16 | 28.6 | 28.62 | 50 | 85.8 | 47.1 | 61.5 | 49.3 | 213.4 | 209.9 | 209.9 | NO
1 | OK | 57 | 70 | 77 | 16 | 28.6 | 27.14 | 50 | 85.8 | 47.1 | 62.7 | 47.2 | 211.7 | 213.8 | 211.7 | YES
2 | OK | 70 | 71 | 77 | 16 | 28.6 | 25.98 | 50 | 85.8 | 47.1 | 63.6 | 47.2 | 210.3 | 213.8 | 210.3 | YES
3 | ** OPTIMAL ** | 71 | 72 | 77 | 16 | 28.6 | 13.51 | 50 | 85.8 | 47.1 | 73.1 | 47.2 | 212 | 213.8 | 212 | YES
| NG | 72 | 79 | 75 | 16 | 31.3 | 13.51 | 50 | 85.8 | 47.1 | 73.1 | 59.3 | 212 | 188.8 | 188.8 | NO
| NG | 79 | 80 | 75 | 16 | 31.3 | 13.04 | 50 | 85.8 | 47.1 | 73.4 | 58.8 | 212.1 | 190.2 | 190.2 | NO
| NG | 80 | 81 | 75 | 16 | 31.3 | 11.68 | 50 | 85.8 | 47.1 | 74.5 | 57.5 | 212.2 | 194 | 194 | NO
| NG | 81 | 95 | 75 | 16 | 31.3 | 11.58 | 50 | 85.8 | 47.1 | 74.6 | 57.4 | 212.1 | 194.2 | 194.2 | NO
| NG | 95 | 120 | 75 | 16 | 31.3 | 11.58 | 50 | 85.8 | 47.1 | 74.6 | 57.4 | 212.1 | 194.2 | 194.2 | NO
| NG | 120 | 88 | 75 | 16 | 31.3 | 10.9 | 50 | 85.8 | 47.1 | 75.1 | 56.7 | 211 | 195.6 | 195.6 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 52-930250
TR_B (available) | 59-022624
TR_A Rated kVA | 160
TR_B Rated kVA | 160
TR_A Baseline Loading% | 85.8
TR_B Baseline Loading% | 47.1
Total Scenarios Evaluated | 33
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 71
Switch Child Node | 72
Tie Node (TR_A side) | 77
Tie Node (TR_B side) | 16
Tie Line Distance (m) | 28.6
Load Transferred (kW) | 13.51
TR_A Loading After (%) | 73.1
TR_B Loading After (%) | 47.2
Minimum Voltage (V) | 212