## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 5 | 6 | 26 | 15 | 19.4 | 86.49 | 50 | 85.8 | 3.5 | 19 | 22.8 | 217.8 | 5 | 5 | NO
| NG | 6 | 8 | 26 | 15 | 19.4 | 84.87 | 50 | 85.8 | 3.5 | 20.2 | 22.8 | 217.8 | 5 | 5 | NO
| NG | 8 | 9 | 26 | 15 | 19.4 | 84.2 | 50 | 85.8 | 3.5 | 20.7 | 22.8 | 217.8 | 5 | 5 | NO
| NG | 9 | 10 | 26 | 15 | 19.4 | 60.56 | 50 | 85.8 | 3.5 | 37.8 | 13.2 | 216.1 | 5.1 | 5.1 | NO
| NG | 9 | 40 | 40 | 13 | 184.1 | 23.64 | 50 | 85.8 | 3.5 | 68.2 | 10 | 181.1 | 205.7 | 181.1 | NO
| NG | 10 | 11 | 26 | 15 | 19.4 | 59.46 | 50 | 85.8 | 3.5 | 38.6 | 13.2 | 216.1 | 5 | 5 | NO
| NG | 11 | 22 | 26 | 15 | 19.4 | 49.4 | 50 | 85.8 | 3.5 | 46.1 | 9.3 | 215.1 | 206.9 | 206.9 | NO
| NG | 11 | 103 | 102 | 11 | 163.2 | 10.06 | 50 | 85.8 | 3.5 | 78.1 | 6.8 | 180.5 | 217.6 | 180.5 | NO
1 | OK | 22 | 101 | 96 | 29 | 38.3 | 40.97 | 50 | 85.8 | 3.5 | 52.2 | 3.5 | 214.8 | 228.8 | 214.8 | YES
| NG | 103 | 102 | 102 | 11 | 163.2 | 9.56 | 50 | 85.8 | 3.5 | 78.5 | 6.8 | 180.2 | 217.6 | 180.2 | NO
2 | ** OPTIMAL ** | 101 | 100 | 96 | 29 | 38.3 | 40.97 | 50 | 85.8 | 3.5 | 52.2 | 3.5 | 214.8 | 228.8 | 214.8 | YES
3 | OK | 100 | 133 | 96 | 29 | 38.3 | 40.54 | 50 | 85.8 | 3.5 | 52.5 | 3.5 | 214.7 | 228.8 | 214.7 | YES
4 | OK | 133 | 132 | 96 | 29 | 38.3 | 40.38 | 50 | 85.8 | 3.5 | 52.7 | 3.5 | 214.7 | 228.8 | 214.7 | YES
5 | OK | 132 | 131 | 96 | 29 | 38.3 | 39.74 | 50 | 85.8 | 3.5 | 53.1 | 3.5 | 214.7 | 228.8 | 214.7 | YES
6 | OK | 131 | 82 | 96 | 29 | 38.3 | 39.74 | 50 | 85.8 | 3.5 | 53 | 3.5 | 214.7 | 228.8 | 214.7 | YES
7 | OK | 82 | 58 | 96 | 29 | 38.3 | 30.12 | 50 | 85.8 | 3.5 | 60.1 | 3.5 | 214 | 228.8 | 214 | YES
8 | OK | 58 | 55 | 96 | 29 | 38.3 | 29.07 | 50 | 85.8 | 3.5 | 61.1 | 3.5 | 213.9 | 228.8 | 213.9 | YES
9 | OK | 55 | 57 | 96 | 29 | 38.3 | 28.62 | 50 | 85.8 | 3.5 | 61.5 | 3.5 | 213.4 | 228.8 | 213.4 | YES
10 | OK | 57 | 70 | 96 | 29 | 38.3 | 27.14 | 50 | 85.8 | 3.5 | 62.7 | 3.5 | 211.7 | 228.8 | 211.7 | YES
11 | OK | 70 | 71 | 96 | 29 | 38.3 | 25.98 | 50 | 85.8 | 3.5 | 63.6 | 3.5 | 210.3 | 228.8 | 210.3 | YES
12 | OK | 71 | 72 | 96 | 29 | 38.3 | 13.51 | 50 | 85.8 | 3.5 | 73.1 | 3.5 | 212 | 228.8 | 212 | YES
| NG | 71 | 59 | 61 | 15 | 128.4 | 12.47 | 50 | 85.8 | 3.5 | 74.9 | 3.5 | 194.8 | 228.8 | 194.8 | NO
13 | OK | 72 | 79 | 96 | 29 | 38.3 | 13.51 | 50 | 85.8 | 3.5 | 73.1 | 3.5 | 212 | 228.8 | 212 | YES
| NG | 59 | 60 | 61 | 15 | 128.4 | 10.7 | 50 | 85.8 | 3.5 | 76.1 | 3.5 | 195 | 228.8 | 195 | NO
14 | OK | 79 | 80 | 96 | 29 | 38.3 | 13.04 | 50 | 85.8 | 3.5 | 73.4 | 3.5 | 212.1 | 228.8 | 212.1 | YES
15 | OK | 80 | 81 | 96 | 29 | 38.3 | 11.68 | 50 | 85.8 | 3.5 | 74.5 | 3.5 | 212.2 | 228.8 | 212.2 | YES
16 | OK | 81 | 95 | 96 | 29 | 38.3 | 11.58 | 50 | 85.8 | 3.5 | 74.6 | 3.5 | 212.1 | 228.8 | 212.1 | YES
17 | OK | 95 | 120 | 120 | 29 | 127.4 | 11.58 | 50 | 85.8 | 3.5 | 74.6 | 3.5 | 212.1 | 228.8 | 212.1 | YES
18 | OK | 120 | 88 | 88 | 29 | 138.8 | 10.9 | 50 | 85.8 | 3.5 | 75.1 | 3.5 | 211 | 228.8 | 211 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 52-930250
TR_B (available) | 65-027398
TR_A Rated kVA | 160
TR_B Rated kVA | 250
TR_A Baseline Loading% | 85.8
TR_B Baseline Loading% | 3.5
Total Scenarios Evaluated | 29
Feasible Scenarios | 18
--- Optimal Solution ---
Switch Parent Node | 101
Switch Child Node | 100
Tie Node (TR_A side) | 96
Tie Node (TR_B side) | 29
Tie Line Distance (m) | 38.3
Load Transferred (kW) | 40.97
TR_A Loading After (%) | 52.2
TR_B Loading After (%) | 3.5
Minimum Voltage (V) | 214.8