## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 28 | 27 | 97 | 19 | 17.9 | 10.33 | 50 | 80 | 68.9 | 72.5 | 70.3 | 212.2 | 208.1 | 208.1 | NO
1 | OK | 28 | 91 | 48 | 21 | 118.3 | 20.62 | 50 | 80 | 68.9 | 64.9 | 70.5 | 211.7 | 213 | 211.7 | YES
| NG | 27 | 29 | 97 | 19 | 17.9 | 9.03 | 50 | 80 | 68.9 | 73.4 | 70.1 | 212.2 | 209.4 | 209.4 | NO
2 | OK | 91 | 78 | 48 | 21 | 118.3 | 9.44 | 50 | 80 | 68.9 | 73.1 | 70.1 | 211.8 | 213.5 | 211.8 | YES
3 | ** OPTIMAL ** | 60 | 59 | 93 | 123 | 1 | 15.82 | 50 | 80 | 68.9 | 68.5 | 76.7 | 211.9 | 212.2 | 211.9 | YES
4 | OK | 60 | 69 | 69 | 121 | 1.2 | 0.14 | 95 | 80 | 68.9 | 79.9 | 68.9 | 211.3 | 213.5 | 211.3 | YES
5 | OK | 60 | 85 | 52 | 21 | 33.1 | 11.89 | 50 | 80 | 68.9 | 71.3 | 70.8 | 211.8 | 212.8 | 211.8 | YES
6 | OK | 29 | 32 | 97 | 19 | 17.9 | 6.49 | 50 | 80 | 68.9 | 75.3 | 69.7 | 211.8 | 211.8 | 211.8 | YES
7 | OK | 78 | 77 | 48 | 21 | 118.3 | 8.1 | 50 | 80 | 68.9 | 74.1 | 70.1 | 211.8 | 213.5 | 211.8 | YES
8 | OK | 59 | 61 | 93 | 123 | 1 | 14.61 | 50 | 80 | 68.9 | 69.3 | 76.1 | 211.9 | 213.2 | 211.9 | YES
9 | OK | 85 | 84 | 52 | 21 | 33.1 | 11.74 | 50 | 80 | 68.9 | 71.4 | 70.8 | 211.8 | 212.8 | 211.8 | YES
10 | OK | 32 | 33 | 97 | 19 | 17.9 | 3.33 | 50 | 80 | 68.9 | 77.6 | 69.7 | 211.5 | 211.8 | 211.5 | YES
11 | OK | 77 | 48 | 48 | 21 | 118.3 | 5.07 | 50 | 80 | 68.9 | 76.3 | 69.6 | 211.6 | 213.5 | 211.6 | YES
| NG | 24 | 22 | 96 | 19 | 86.6 | 10.82 | 50 | 80 | 68.9 | 71.9 | 71.1 | 212.7 | 202.3 | 202.3 | NO
12 | OK | 61 | 62 | 93 | 123 | 1 | 13.13 | 50 | 80 | 68.9 | 70.4 | 75.3 | 211.9 | 213.3 | 211.9 | YES
13 | OK | 84 | 53 | 52 | 21 | 33.1 | 11.07 | 50 | 80 | 68.9 | 71.9 | 70.6 | 211.8 | 213.5 | 211.8 | YES
14 | OK | 33 | 35 | 97 | 19 | 17.9 | 2.78 | 50 | 80 | 68.9 | 78 | 69.7 | 211.5 | 211.8 | 211.5 | YES
15 | OK | 48 | 47 | 47 | 21 | 118.6 | 4.7 | 50 | 80 | 68.9 | 76.5 | 69.6 | 211.6 | 213.5 | 211.6 | YES
| NG | 22 | 21 | 96 | 19 | 86.6 | 6.01 | 50 | 80 | 68.9 | 75.5 | 70.3 | 211.9 | 208.1 | 208.1 | NO
16 | OK | 62 | 65 | 93 | 123 | 1 | 12.73 | 50 | 80 | 68.9 | 70.7 | 75.1 | 211.9 | 213.3 | 211.9 | YES
17 | OK | 53 | 52 | 52 | 21 | 33.1 | 9.22 | 50 | 80 | 68.9 | 73.3 | 69.9 | 211.6 | 213.5 | 211.6 | YES
18 | OK | 35 | 34 | 97 | 19 | 17.9 | 1.66 | 50 | 80 | 68.9 | 78.8 | 69.7 | 211.2 | 211.8 | 211.2 | YES
19 | OK | 47 | 81 | 81 | 21 | 128.6 | 3.68 | 50 | 80 | 68.9 | 77.3 | 69.3 | 211.5 | 213.5 | 211.5 | YES
20 | OK | 47 | 80 | 80 | 21 | 140.9 | 0.57 | 50 | 80 | 68.9 | 79.6 | 69.1 | 211.4 | 213.5 | 211.4 | YES
| NG | 21 | 20 | 96 | 19 | 86.6 | 4.43 | 50 | 80 | 68.9 | 76.7 | 70.3 | 211.5 | 208.1 | 208.1 | NO
21 | OK | 65 | 64 | 92 | 88 | 35.4 | 5.25 | 50 | 80 | 68.9 | 76.1 | 71.5 | 211.5 | 212.9 | 211.5 | YES
22 | OK | 65 | 63 | 63 | 20 | 116.7 | 4.32 | 50 | 80 | 68.9 | 76.8 | 71.1 | 211.7 | 210.3 | 210.3 | YES
23 | OK | 65 | 105 | 93 | 123 | 1 | 3.16 | 50 | 80 | 68.9 | 77.6 | 70.4 | 211.3 | 213.5 | 211.3 | YES
24 | OK | 52 | 86 | 86 | 21 | 34.5 | 7.13 | 50 | 80 | 68.9 | 74.7 | 69.9 | 211.6 | 213.5 | 211.6 | YES
25 | OK | 52 | 87 | 87 | 21 | 53.5 | 1.99 | 50 | 80 | 68.9 | 78.6 | 69.9 | 211.3 | 213.5 | 211.3 | YES
26 | OK | 34 | 97 | 97 | 19 | 17.9 | 1.66 | 50 | 80 | 68.9 | 78.8 | 69 | 211.2 | 213.5 | 211.2 | YES
27 | OK | 81 | 82 | 82 | 21 | 152.2 | 3.48 | 50 | 80 | 68.9 | 77.4 | 69.3 | 211.5 | 213.5 | 211.5 | YES
28 | OK | 80 | 79 | 79 | 21 | 167.6 | 0.44 | 50 | 80 | 68.9 | 79.7 | 69.1 | 211.4 | 213.5 | 211.4 | YES
| NG | 20 | 18 | 96 | 19 | 86.6 | 3.17 | 50 | 80 | 68.9 | 77.6 | 70.3 | 211 | 208.1 | 208.1 | NO
29 | OK | 64 | 66 | 92 | 88 | 35.4 | 2.32 | 50 | 80 | 68.9 | 78.3 | 70 | 211.4 | 213.4 | 211.4 | YES
30 | OK | 63 | 30 | 30 | 19 | 117.1 | 1.92 | 50 | 80 | 68.9 | 78.6 | 69.8 | 211.5 | 212.6 | 211.5 | YES
31 | OK | 105 | 94 | 93 | 123 | 1 | 2.32 | 50 | 80 | 68.9 | 77.6 | 70 | 211.3 | 213.5 | 211.3 | YES
32 | OK | 86 | 88 | 54 | 6 | 47.4 | 6.29 | 50 | 80 | 68.9 | 75.4 | 70.2 | 211.6 | 213.5 | 211.6 | YES
33 | OK | 87 | 51 | 51 | 21 | 95.1 | 1.6 | 50 | 80 | 68.9 | 78.8 | 69.7 | 211.3 | 213.5 | 211.3 | YES
34 | OK | 82 | 83 | 43 | 6 | 167.7 | 1.92 | 50 | 80 | 68.9 | 78.6 | 69.2 | 211.4 | 213.5 | 211.4 | YES
| NG | 18 | 19 | 96 | 19 | 86.6 | 2.95 | 50 | 80 | 68.9 | 77.8 | 70.3 | 211 | 208.1 | 208.1 | NO
35 | OK | 66 | 92 | 92 | 88 | 35.4 | 0.87 | 50 | 80 | 68.9 | 79.4 | 68.9 | 211.3 | 213.5 | 211.3 | YES
36 | OK | 30 | 31 | 31 | 19 | 128.4 | 1.19 | 50 | 80 | 68.9 | 79.1 | 69.5 | 211.4 | 213.4 | 211.4 | YES
37 | OK | 88 | 89 | 54 | 6 | 47.4 | 6.12 | 50 | 80 | 68.9 | 75.5 | 70.2 | 211.6 | 213.5 | 211.6 | YES
38 | OK | 83 | 44 | 43 | 6 | 167.7 | 0.49 | 50 | 80 | 68.9 | 79.6 | 68.9 | 211.4 | 213.5 | 211.4 | YES
| NG | 19 | 16 | 96 | 19 | 86.6 | 2.68 | 50 | 80 | 68.9 | 78 | 70.3 | 210.9 | 208.1 | 208.1 | NO
39 | OK | 89 | 90 | 54 | 6 | 47.4 | 4.76 | 50 | 80 | 68.9 | 76.5 | 70.2 | 211.4 | 213.5 | 211.4 | YES
40 | OK | 44 | 43 | 43 | 6 | 167.7 | 0.45 | 50 | 80 | 68.9 | 79.7 | 68.9 | 211.4 | 213.5 | 211.4 | YES
41 | OK | 16 | 17 | 96 | 19 | 86.6 | 1.24 | 50 | 80 | 68.9 | 79.1 | 69.5 | 211.1 | 212.6 | 211.1 | YES
42 | OK | 90 | 50 | 54 | 6 | 47.4 | 3.21 | 50 | 80 | 68.9 | 77.6 | 70.2 | 211.3 | 213.5 | 211.3 | YES
43 | OK | 17 | 96 | 96 | 19 | 86.6 | 1.18 | 50 | 80 | 68.9 | 79.1 | 69.5 | 211.1 | 212.8 | 211.1 | YES
44 | OK | 50 | 49 | 54 | 6 | 47.4 | 2.83 | 50 | 80 | 68.9 | 77.9 | 70.2 | 211.3 | 213.5 | 211.3 | YES
45 | OK | 96 | 104 | 104 | 0 | 112.7 | 1.17 | 50 | 80 | 68.9 | 79.1 | 69.5 | 211.1 | 213.5 | 211.1 | YES
46 | OK | 49 | 55 | 55 | 6 | 117.5 | 1.86 | 50 | 80 | 68.9 | 78.6 | 69.8 | 211.3 | 213.5 | 211.3 | YES
47 | OK | 49 | 54 | 54 | 6 | 47.4 | 0.81 | 50 | 80 | 68.9 | 79.4 | 69.3 | 211.3 | 213.5 | 211.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 52-940032
TR_B (available) | 60-033423
TR_A Rated kVA | 160
TR_B Rated kVA | 250
TR_A Baseline Loading% | 80
TR_B Baseline Loading% | 68.9
Total Scenarios Evaluated | 55
Feasible Scenarios | 47
--- Optimal Solution ---
Switch Parent Node | 60
Switch Child Node | 59
Tie Node (TR_A side) | 93
Tie Node (TR_B side) | 123
Tie Line Distance (m) | 1
Load Transferred (kW) | 15.82
TR_A Loading After (%) | 68.5
TR_B Loading After (%) | 76.7
Minimum Voltage (V) | 211.9