## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 12 | 11 | 11 | 3 | 193.5 | 6.41 | 50 | 80.3 | 36.3 | 55.3 | 62 | 213.1 | 208.1 | 208.1 | NO
| NG | 12 | 13 | 16 | 3 | 3.7 | 13.01 | 50 | 80.3 | 36.3 | 24.9 | 88.5 | 220.7 | 205.4 | 205.4 | NO
| NG | 13 | 14 | 16 | 3 | 3.7 | 13.01 | 50 | 80.3 | 36.3 | 29.1 | 88.5 | 219.9 | 205.4 | 205.4 | NO
| NG | 14 | 19 | 16 | 3 | 3.7 | 12.71 | 50 | 80.3 | 36.3 | 30.2 | 87.4 | 219.9 | 205.4 | 205.4 | NO
| NG | 19 | 20 | 16 | 3 | 3.7 | 11.12 | 50 | 80.3 | 36.3 | 36.3 | 80.7 | 218.8 | 208.7 | 208.7 | NO
| NG | 20 | 16 | 16 | 3 | 3.7 | 11.12 | 50 | 80.3 | 36.3 | 36.3 | 80.7 | 218.8 | 208.7 | 208.7 | NO
| NG | 16 | 17 | 17 | 3 | 28.2 | 11.12 | 50 | 80.3 | 36.3 | 36.3 | 80.6 | 218.8 | 208.8 | 208.8 | NO
| NG | 17 | 21 | 21 | 3 | 65.9 | 11 | 50 | 80.3 | 36.3 | 36.8 | 80.1 | 218.7 | 209.1 | 209.1 | NO
1 | OK | 21 | 22 | 22 | 3 | 102.1 | 2.75 | 50 | 80.3 | 36.3 | 69.6 | 46.9 | 210.6 | 222.8 | 210.6 | YES
2 | ** OPTIMAL ** | 22 | 23 | 23 | 3 | 142.7 | 0.41 | 50 | 80.3 | 36.3 | 78.6 | 37.8 | 210.8 | 224.1 | 210.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 53-008425
TR_B (available) | 55-000546
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 80.3
TR_B Baseline Loading% | 36.3
Total Scenarios Evaluated | 10
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 22
Switch Child Node | 23
Tie Node (TR_A side) | 23
Tie Node (TR_B side) | 3
Tie Line Distance (m) | 142.7
Load Transferred (kW) | 0.41
TR_A Loading After (%) | 78.6
TR_B Loading After (%) | 37.8
Minimum Voltage (V) | 210.8