## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 3 | 4 | 22 | 17 | 122.6 | 14.4 | 50 | 86.9 | 22 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 4 | 0 | 22 | 17 | 122.6 | 14.4 | 50 | 86.9 | 22 | 29.5 | 59 | 224 | 194.7 | 194.7 | NO
| NG | 0 | 1 | 22 | 17 | 122.6 | 13.65 | 50 | 86.9 | 22 | 32.3 | 56.8 | 223.4 | 200.3 | 200.3 | NO
| NG | 1 | 27 | 22 | 17 | 122.6 | 12.9 | 50 | 86.9 | 22 | 35.2 | 54.6 | 223.3 | 201.1 | 201.1 | NO
| NG | 27 | 26 | 22 | 17 | 122.6 | 12.22 | 50 | 86.9 | 22 | 37.8 | 52.8 | 223.3 | 200.7 | 200.7 | NO
| NG | 26 | 18 | 22 | 17 | 122.6 | 12.22 | 50 | 86.9 | 22 | 37.8 | 52.8 | 223.3 | 200.7 | 200.7 | NO
| NG | 18 | 19 | 22 | 17 | 122.6 | 11.68 | 50 | 86.9 | 22 | 39.9 | 51.3 | 223.1 | 202.1 | 202.1 | NO
| NG | 19 | 20 | 22 | 17 | 122.6 | 11.01 | 50 | 86.9 | 22 | 42.4 | 49.4 | 222.6 | 205.8 | 205.8 | NO
| NG | 20 | 9 | 22 | 17 | 122.6 | 9.43 | 50 | 86.9 | 22 | 48.5 | 45.3 | 222.6 | 205.7 | 205.7 | NO
| NG | 9 | 10 | 22 | 17 | 122.6 | 9.13 | 50 | 86.9 | 22 | 49.7 | 44.6 | 222.3 | 205.6 | 205.6 | NO
| NG | 10 | 21 | 22 | 17 | 122.6 | 7.74 | 50 | 86.9 | 22 | 55.2 | 41 | 220.5 | 208.4 | 208.4 | NO
| NG | 21 | 23 | 22 | 17 | 122.6 | 7.74 | 50 | 86.9 | 22 | 55.2 | 41 | 220.5 | 208.4 | 208.4 | NO
1 | OK | 23 | 24 | 22 | 17 | 122.6 | 5.84 | 50 | 86.9 | 22 | 62.7 | 36.3 | 217 | 210.9 | 210.9 | YES
2 | OK | 24 | 25 | 22 | 17 | 122.6 | 3.94 | 50 | 86.9 | 22 | 70.4 | 31.5 | 215.7 | 215.9 | 215.7 | YES
3 | ** OPTIMAL ** | 25 | 13 | 22 | 17 | 122.6 | 3.94 | 50 | 86.9 | 22 | 70.4 | 31.5 | 215.7 | 215.9 | 215.7 | YES
4 | OK | 13 | 14 | 22 | 17 | 122.6 | 2.54 | 50 | 86.9 | 22 | 76.1 | 28.1 | 212.6 | 220.5 | 212.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 53-009921
TR_B (available) | 66-015198
TR_A Rated kVA | 30
TR_B Rated kVA | 50
TR_A Baseline Loading% | 86.9
TR_B Baseline Loading% | 22
Total Scenarios Evaluated | 16
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 25
Switch Child Node | 13
Tie Node (TR_A side) | 22
Tie Node (TR_B side) | 17
Tie Line Distance (m) | 122.6
Load Transferred (kW) | 3.94
TR_A Loading After (%) | 70.4
TR_B Loading After (%) | 31.5
Minimum Voltage (V) | 215.7