## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 61 | 8 | 64 | 18 | 2.9 | 24.82 | 50 | 86.8 | 26.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 8 | 2 | 64 | 18 | 2.9 | 24.66 | 50 | 86.8 | 26.2 | 29.4 | 86.2 | 222.8 | 198.8 | 198.8 | NO
1 | ** OPTIMAL ** | 2 | 19 | 64 | 18 | 2.9 | 13.8 | 50 | 86.8 | 26.2 | 36.7 | 58.5 | 222.7 | 219.5 | 219.5 | YES
2 | OK | 19 | 18 | 64 | 18 | 2.9 | 13.8 | 50 | 86.8 | 26.2 | 54.5 | 58.5 | 219.9 | 219.5 | 219.5 | YES
3 | OK | 18 | 7 | 64 | 18 | 2.9 | 12.62 | 50 | 86.8 | 26.2 | 54.5 | 55.7 | 219.9 | 219.2 | 219.2 | YES
4 | OK | 7 | 6 | 64 | 18 | 2.9 | 11.68 | 50 | 86.8 | 26.2 | 59.4 | 53.5 | 219.8 | 219.4 | 219.4 | YES
5 | OK | 6 | 26 | 64 | 18 | 2.9 | 8.7 | 50 | 86.8 | 26.2 | 66.3 | 46.4 | 219.2 | 221.2 | 219.2 | YES
| NG | 26 | 65 | 64 | 18 | 2.9 | 8.7 | 50 | 86.8 | 26.2 | 66.3 | 170.7 | 219.2 | 6.5 | 6.5 | NO
6 | OK | 65 | 64 | 64 | 18 | 2.9 | 8.06 | 50 | 86.8 | 26.2 | 67.8 | 44.9 | 219.2 | 221 | 219.2 | YES
| NG | 64 | 94 | 94 | 18 | 4.5 | 7.39 | 50 | 86.8 | 26.2 | 192.6 | 43.4 | 19.7 | 221 | 19.7 | NO
7 | OK | 94 | 92 | 92 | 18 | 43.3 | 7.16 | 50 | 86.8 | 26.2 | 69.9 | 42.8 | 219 | 221.3 | 219 | YES
8 | OK | 92 | 27 | 27 | 18 | 48.5 | 7.16 | 50 | 86.8 | 26.2 | 69.9 | 42.4 | 219 | 221.6 | 219 | YES
9 | OK | 27 | 28 | 28 | 18 | 91.1 | 6.99 | 50 | 86.8 | 26.2 | 70.3 | 42.4 | 219 | 221.6 | 219 | YES
10 | OK | 28 | 86 | 86 | 18 | 93.9 | 5.86 | 50 | 86.8 | 26.2 | 70.3 | 39.8 | 219 | 221.3 | 219 | YES
11 | OK | 86 | 90 | 90 | 18 | 100 | 5.63 | 50 | 86.8 | 26.2 | 73.4 | 39.3 | 219 | 221.6 | 219 | YES
12 | OK | 90 | 91 | 91 | 18 | 100.8 | 3.89 | 50 | 86.8 | 26.2 | 77.5 | 34.9 | 219 | 221.2 | 219 | YES
13 | OK | 91 | 96 | 96 | 18 | 108.2 | 3.76 | 50 | 86.8 | 26.2 | 77.8 | 34.9 | 219 | 221.3 | 219 | YES
14 | OK | 96 | 75 | 75 | 18 | 114.6 | 3.45 | 50 | 86.8 | 26.2 | 78.5 | 34.2 | 219 | 221.2 | 219 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 53-010380
TR_B (available) | 58-009023
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 86.8
TR_B Baseline Loading% | 26.2
Total Scenarios Evaluated | 18
Feasible Scenarios | 14
--- Optimal Solution ---
Switch Parent Node | 2
Switch Child Node | 19
Tie Node (TR_A side) | 64
Tie Node (TR_B side) | 18
Tie Line Distance (m) | 2.9
Load Transferred (kW) | 13.8
TR_A Loading After (%) | 36.7
TR_B Loading After (%) | 58.5
Minimum Voltage (V) | 219.5