## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 1 | 2 | 35 | 31 | 4 | 21.2 | 50 | 70.4 | 33 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 2 | 8 | 35 | 31 | 4 | 19.82 | 50 | 70.4 | 33 | 24.3 | 56.5 | 226.5 | 210.4 | 210.4 | YES
2 | ** OPTIMAL ** | 8 | 27 | 35 | 31 | 4 | 11.02 | 50 | 70.4 | 33 | 44.7 | 45.8 | 220.9 | 220.6 | 220.6 | YES
3 | OK | 27 | 18 | 35 | 31 | 4 | 10.28 | 50 | 70.4 | 33 | 46.4 | 44.9 | 221 | 220.6 | 220.6 | YES
4 | OK | 18 | 16 | 35 | 31 | 4 | 10.02 | 50 | 70.4 | 33 | 47 | 44.6 | 221 | 220.6 | 220.6 | YES
5 | OK | 16 | 24 | 35 | 31 | 4 | 10.02 | 50 | 70.4 | 33 | 47 | 44.6 | 221 | 220.6 | 220.6 | YES
6 | OK | 24 | 25 | 35 | 31 | 4 | 9.17 | 50 | 70.4 | 33 | 49 | 43.6 | 221 | 220.6 | 220.6 | YES
7 | OK | 25 | 22 | 35 | 31 | 4 | 9.17 | 50 | 70.4 | 33 | 49 | 43.6 | 221 | 220.6 | 220.6 | YES
8 | OK | 22 | 23 | 23 | 31 | 144.1 | 1.64 | 50 | 70.4 | 33 | 66.5 | 34.9 | 219.2 | 221.4 | 219.2 | YES
9 | OK | 22 | 38 | 35 | 31 | 4 | 5.73 | 50 | 70.4 | 33 | 57 | 39.6 | 219.8 | 221.1 | 219.8 | YES
10 | OK | 38 | 26 | 35 | 31 | 4 | 4.82 | 50 | 70.4 | 33 | 59.1 | 38.5 | 219.3 | 221.3 | 219.3 | YES
11 | OK | 26 | 13 | 35 | 31 | 4 | 3.15 | 50 | 70.4 | 33 | 63 | 36.6 | 219 | 221.4 | 219 | YES
12 | OK | 13 | 14 | 35 | 31 | 4 | 2.46 | 50 | 70.4 | 33 | 64.6 | 35.5 | 218.5 | 221.6 | 218.5 | YES
13 | OK | 13 | 39 | 39 | 31 | 57.2 | 0.69 | 50 | 70.4 | 33 | 68.8 | 33.8 | 218.3 | 221.7 | 218.3 | YES
14 | OK | 14 | 35 | 35 | 31 | 4 | 2.2 | 50 | 70.4 | 33 | 65.3 | 35.5 | 218.5 | 221.6 | 218.5 | YES
15 | OK | 39 | 15 | 15 | 52 | 149.7 | 0.67 | 50 | 70.4 | 33 | 68.8 | 33.8 | 218.3 | 221.7 | 218.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 54-004185
TR_B (available) | 60-025364
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 70.4
TR_B Baseline Loading% | 33
Total Scenarios Evaluated | 16
Feasible Scenarios | 15
--- Optimal Solution ---
Switch Parent Node | 8
Switch Child Node | 27
Tie Node (TR_A side) | 35
Tie Node (TR_B side) | 31
Tie Line Distance (m) | 4
Load Transferred (kW) | 11.02
TR_A Loading After (%) | 44.7
TR_B Loading After (%) | 45.8
Minimum Voltage (V) | 220.6