## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 1 | 2 | 34 | 1 | 18.6 | 21.2 | 50 | 70.4 | 26.1 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 2 | 8 | 34 | 1 | 18.6 | 19.82 | 50 | 70.4 | 26.1 | 24.3 | 51 | 226.5 | 200.6 | 200.6 | NO
1 | ** OPTIMAL ** | 8 | 27 | 20 | 13 | 27.1 | 11.02 | 50 | 70.4 | 26.1 | 44.7 | 31.1 | 220.9 | 220 | 220 | YES
2 | OK | 8 | 30 | 34 | 1 | 18.6 | 8.44 | 50 | 70.4 | 26.1 | 50.7 | 36.2 | 221.8 | 219.6 | 219.6 | YES
3 | OK | 27 | 18 | 20 | 13 | 27.1 | 10.28 | 50 | 70.4 | 26.1 | 46.4 | 31.1 | 221 | 220 | 220 | YES
4 | OK | 30 | 31 | 34 | 1 | 18.6 | 8.39 | 50 | 70.4 | 26.1 | 50.8 | 36.1 | 221.8 | 219.6 | 219.6 | YES
5 | OK | 18 | 16 | 20 | 13 | 27.1 | 10.02 | 50 | 70.4 | 26.1 | 47 | 31.1 | 221 | 220 | 220 | YES
6 | OK | 31 | 9 | 34 | 1 | 18.6 | 8.39 | 50 | 70.4 | 26.1 | 50.8 | 36.1 | 221.8 | 219.6 | 219.6 | YES
7 | OK | 16 | 24 | 20 | 13 | 27.1 | 10.02 | 50 | 70.4 | 26.1 | 47 | 31.1 | 221 | 220 | 220 | YES
8 | OK | 9 | 10 | 34 | 1 | 18.6 | 7.72 | 50 | 70.4 | 26.1 | 52.3 | 35.3 | 221.8 | 219.2 | 219.2 | YES
9 | OK | 24 | 25 | 20 | 13 | 27.1 | 9.17 | 50 | 70.4 | 26.1 | 49 | 31.1 | 221 | 220 | 220 | YES
10 | OK | 10 | 29 | 34 | 1 | 18.6 | 5.3 | 50 | 70.4 | 26.1 | 58 | 32.4 | 219.9 | 218.6 | 218.6 | YES
11 | OK | 25 | 22 | 20 | 13 | 27.1 | 9.17 | 50 | 70.4 | 26.1 | 49 | 31.1 | 221 | 220 | 220 | YES
12 | OK | 29 | 11 | 34 | 1 | 18.6 | 4.33 | 50 | 70.4 | 26.1 | 60.2 | 31.2 | 219.9 | 221.3 | 219.9 | YES
13 | OK | 22 | 23 | 20 | 13 | 27.1 | 1.64 | 50 | 70.4 | 26.1 | 66.5 | 28 | 219.2 | 223.5 | 219.2 | YES
14 | OK | 22 | 38 | 15 | 12 | 69 | 5.73 | 50 | 70.4 | 26.1 | 57 | 29.1 | 219.8 | 223.7 | 219.8 | YES
15 | OK | 11 | 12 | 34 | 1 | 18.6 | 1.84 | 50 | 70.4 | 26.1 | 66.1 | 28.3 | 218.5 | 220.7 | 218.5 | YES
16 | OK | 38 | 26 | 15 | 12 | 69 | 4.82 | 50 | 70.4 | 26.1 | 59.1 | 28.4 | 219.3 | 223.6 | 219.3 | YES
17 | OK | 12 | 32 | 34 | 1 | 18.6 | 0.91 | 50 | 70.4 | 26.1 | 68.3 | 27.2 | 218.6 | 223 | 218.6 | YES
18 | OK | 26 | 13 | 15 | 12 | 69 | 3.15 | 50 | 70.4 | 26.1 | 63 | 27.8 | 219 | 223.5 | 219 | YES
19 | OK | 32 | 33 | 34 | 1 | 18.6 | 0.67 | 50 | 70.4 | 26.1 | 68.8 | 26.9 | 218.7 | 223 | 218.7 | YES
20 | OK | 13 | 39 | 15 | 12 | 69 | 0.69 | 50 | 70.4 | 26.1 | 68.8 | 26.8 | 218.3 | 223.4 | 218.3 | YES
21 | OK | 33 | 34 | 34 | 1 | 18.6 | 0.46 | 50 | 70.4 | 26.1 | 69.3 | 26.7 | 218.7 | 223.3 | 218.7 | YES
22 | OK | 39 | 15 | 15 | 12 | 69 | 0.67 | 50 | 70.4 | 26.1 | 68.8 | 26.8 | 218.3 | 223.4 | 218.3 | YES
23 | OK | 34 | 40 | 40 | 1 | 20.7 | 0.33 | 50 | 70.4 | 26.1 | 69.3 | 26.5 | 218.7 | 223.3 | 218.7 | YES
24 | OK | 40 | 41 | 41 | 1 | 104.7 | 0.33 | 50 | 70.4 | 26.1 | 69.6 | 26.5 | 218.8 | 223.3 | 218.8 | YES
25 | OK | 41 | 52 | 52 | 1 | 131.3 | 0.29 | 50 | 70.4 | 26.1 | 69.7 | 26.5 | 218.8 | 223.4 | 218.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 54-004185
TR_B (available) | 63-027435
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 70.4
TR_B Baseline Loading% | 26.1
Total Scenarios Evaluated | 27
Feasible Scenarios | 25
--- Optimal Solution ---
Switch Parent Node | 8
Switch Child Node | 27
Tie Node (TR_A side) | 20
Tie Node (TR_B side) | 13
Tie Line Distance (m) | 27.1
Load Transferred (kW) | 11.02
TR_A Loading After (%) | 44.7
TR_B Loading After (%) | 31.1
Minimum Voltage (V) | 220