## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 27 | 28 | 52 | 142 | 3.3 | 18.95 | 50 | 72.5 | 64 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 28 | 95 | 52 | 142 | 3.3 | 18.91 | 50 | 72.5 | 64 | 28.7 | 71.2 | 225.7 | 173.2 | 173.2 | NO
| NG | 95 | 0 | 52 | 142 | 3.3 | 18.52 | 50 | 72.5 | 64 | 29.6 | 71.2 | 225.7 | 173.2 | 173.2 | NO
| NG | 0 | 2 | 52 | 142 | 3.3 | 6.33 | 50 | 72.5 | 64 | 57.8 | 66.1 | 221.7 | 208.5 | 208.5 | NO
1 | OK | 0 | 5 | 4 | 96 | 160.4 | 5.02 | 50 | 72.5 | 64 | 60.9 | 64.2 | 219.2 | 215.8 | 215.8 | YES
| NG | 2 | 42 | 52 | 142 | 3.3 | 6.17 | 50 | 72.5 | 64 | 58.2 | 66.1 | 221.7 | 208.5 | 208.5 | NO
2 | OK | 5 | 44 | 4 | 96 | 160.4 | 4.97 | 50 | 72.5 | 64 | 61 | 64.2 | 219.2 | 215.8 | 215.8 | YES
| NG | 42 | 43 | 52 | 142 | 3.3 | 5.51 | 50 | 72.5 | 64 | 59.7 | 66.1 | 221.8 | 208.5 | 208.5 | NO
3 | OK | 44 | 45 | 4 | 96 | 160.4 | 1.34 | 50 | 72.5 | 64 | 69.4 | 64.2 | 219.3 | 215.8 | 215.8 | YES
| NG | 43 | 32 | 52 | 142 | 3.3 | 2.58 | 50 | 72.5 | 64 | 66.5 | 66.1 | 222 | 208.5 | 208.5 | NO
4 | OK | 45 | 77 | 4 | 96 | 160.4 | 1.1 | 50 | 72.5 | 64 | 70 | 64.2 | 219.3 | 215.8 | 215.8 | YES
5 | OK | 32 | 31 | 52 | 142 | 3.3 | 1.81 | 50 | 72.5 | 64 | 68.2 | 65.5 | 221.4 | 211.5 | 211.5 | YES
6 | OK | 77 | 6 | 4 | 96 | 160.4 | 1.08 | 50 | 72.5 | 64 | 70 | 64.2 | 219.3 | 215.8 | 215.8 | YES
7 | OK | 31 | 64 | 52 | 142 | 3.3 | 1.81 | 50 | 72.5 | 64 | 68.2 | 65.5 | 221.4 | 211.5 | 211.5 | YES
8 | ** OPTIMAL ** | 6 | 3 | 4 | 96 | 160.4 | 1.08 | 50 | 72.5 | 64 | 70 | 64.2 | 219.3 | 215.8 | 215.8 | YES
9 | OK | 64 | 65 | 52 | 142 | 3.3 | 1.69 | 50 | 72.5 | 64 | 68.5 | 65.4 | 221.3 | 211.9 | 211.9 | YES
10 | OK | 65 | 66 | 52 | 142 | 3.3 | 1.62 | 50 | 72.5 | 64 | 68.7 | 65.3 | 221.2 | 212.2 | 212.2 | YES
11 | OK | 66 | 84 | 52 | 142 | 3.3 | 1.62 | 50 | 72.5 | 64 | 68.7 | 65.3 | 221.2 | 212.2 | 212.2 | YES
12 | OK | 84 | 53 | 52 | 142 | 3.3 | 1.5 | 50 | 72.5 | 64 | 69 | 65.2 | 221.1 | 212.6 | 212.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 54-004521
TR_B (available) | 41-002305
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 72.5
TR_B Baseline Loading% | 64
Total Scenarios Evaluated | 19
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 6
Switch Child Node | 3
Tie Node (TR_A side) | 4
Tie Node (TR_B side) | 96
Tie Line Distance (m) | 160.4
Load Transferred (kW) | 1.08
TR_A Loading After (%) | 70
TR_B Loading After (%) | 64.2
Minimum Voltage (V) | 215.8