## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | ** OPTIMAL ** | 27 | 46 | 80 | 12 | 12.3 | 12.46 | 50 | 72.5 | 9.2 | 43.9 | 19.5 | 221.6 | 220 | 220 | YES
2 | OK | 46 | 18 | 80 | 12 | 12.3 | 10.9 | 50 | 72.5 | 9.2 | 47.5 | 19.5 | 221.7 | 220 | 220 | YES
3 | OK | 18 | 9 | 80 | 12 | 12.3 | 4.23 | 50 | 72.5 | 9.2 | 62.8 | 14.6 | 219.6 | 223 | 219.6 | YES
4 | OK | 9 | 10 | 80 | 12 | 12.3 | 3.55 | 50 | 72.5 | 9.2 | 64.3 | 14.6 | 219.6 | 223 | 219.6 | YES
5 | OK | 10 | 11 | 80 | 12 | 12.3 | 2.39 | 50 | 72.5 | 9.2 | 64.3 | 14.6 | 219.6 | 223 | 219.6 | YES
6 | OK | 11 | 19 | 80 | 12 | 12.3 | 0.87 | 50 | 72.5 | 9.2 | 70.5 | 12.4 | 219.1 | 223.4 | 219.1 | YES
7 | OK | 19 | 20 | 80 | 12 | 12.3 | 0.86 | 50 | 72.5 | 9.2 | 70.5 | 12.4 | 219.1 | 223.4 | 219.1 | YES
8 | OK | 20 | 87 | 80 | 12 | 12.3 | 0.86 | 50 | 72.5 | 9.2 | 70.5 | 12.4 | 219.1 | 223.4 | 219.1 | YES
9 | OK | 87 | 88 | 80 | 12 | 12.3 | 0.86 | 50 | 72.5 | 9.2 | 70.5 | 12.4 | 219.1 | 223.4 | 219.1 | YES
10 | OK | 88 | 89 | 80 | 12 | 12.3 | 0.86 | 50 | 72.5 | 9.2 | 70.5 | 12.4 | 219.1 | 223.4 | 219.1 | YES
11 | OK | 89 | 92 | 80 | 12 | 12.3 | 0.86 | 50 | 72.5 | 9.2 | 70.5 | 12.4 | 219.1 | 223.4 | 219.1 | YES
12 | OK | 92 | 96 | 80 | 12 | 12.3 | 0.86 | 50 | 72.5 | 9.2 | 70.5 | 12.4 | 219.1 | 223.4 | 219.1 | YES
13 | OK | 96 | 91 | 80 | 12 | 12.3 | 0.86 | 50 | 72.5 | 9.2 | 70.5 | 12.4 | 219.1 | 223.4 | 219.1 | YES
14 | OK | 91 | 86 | 80 | 12 | 12.3 | 0.18 | 50 | 72.5 | 9.2 | 72.1 | 9.8 | 219.1 | 223.9 | 219.1 | YES
15 | OK | 86 | 75 | 80 | 12 | 12.3 | 0.18 | 50 | 72.5 | 9.2 | 72.1 | 9.8 | 219.1 | 223.9 | 219.1 | YES
16 | OK | 75 | 76 | 80 | 12 | 12.3 | 0.18 | 50 | 72.5 | 9.2 | 72.1 | 9.8 | 219.1 | 223.9 | 219.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 54-004521
TR_B (available) | 65-009199
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 72.5
TR_B Baseline Loading% | 9.2
Total Scenarios Evaluated | 16
Feasible Scenarios | 16
--- Optimal Solution ---
Switch Parent Node | 27
Switch Child Node | 46
Tie Node (TR_A side) | 80
Tie Node (TR_B side) | 12
Tie Line Distance (m) | 12.3
Load Transferred (kW) | 12.46
TR_A Loading After (%) | 43.9
TR_B Loading After (%) | 19.5
Minimum Voltage (V) | 220