## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 0 | 5 | 4 | 1 | 127.2 | 5.02 | 50 | 72.5 | 22.2 | 60.9 | 36.4 | 219.2 | 218.7 | 218.7 | YES
2 | OK | 5 | 44 | 4 | 1 | 127.2 | 4.97 | 50 | 72.5 | 22.2 | 61 | 36.4 | 219.2 | 218.7 | 218.7 | YES
3 | OK | 44 | 45 | 4 | 1 | 127.2 | 1.34 | 50 | 72.5 | 22.2 | 69.4 | 22.2 | 219.3 | 223.5 | 219.3 | YES
4 | OK | 45 | 77 | 4 | 1 | 127.2 | 1.1 | 50 | 72.5 | 22.2 | 70 | 22.2 | 219.3 | 223.5 | 219.3 | YES
5 | OK | 77 | 6 | 4 | 1 | 127.2 | 1.08 | 50 | 72.5 | 22.2 | 70 | 22.2 | 219.3 | 223.5 | 219.3 | YES
6 | ** OPTIMAL ** | 6 | 3 | 4 | 1 | 127.2 | 1.08 | 50 | 72.5 | 22.2 | 70 | 22.2 | 219.3 | 223.5 | 219.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 54-004521
TR_B (available) | 68-018505
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 72.5
TR_B Baseline Loading% | 22.2
Total Scenarios Evaluated | 6
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 6
Switch Child Node | 3
Tie Node (TR_A side) | 4
Tie Node (TR_B side) | 1
Tie Line Distance (m) | 127.2
Load Transferred (kW) | 1.08
TR_A Loading After (%) | 70
TR_B Loading After (%) | 22.2
Minimum Voltage (V) | 219.3