## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 9 | 8 | 16 | 9 | 84.5 | 12.4 | 50 | 88.7 | 5.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 9 | 10 | 10 | 9 | 87.6 | 10.59 | 50 | 88.7 | 5.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | ** OPTIMAL ** | 8 | 14 | 16 | 9 | 84.5 | 10.98 | 50 | 88.7 | 5.9 | 42.1 | 11.1 | 222.3 | 223.1 | 222.3 | YES
2 | OK | 10 | 11 | 11 | 9 | 129.6 | 10.59 | 50 | 88.7 | 5.9 | 47.8 | 10.8 | 220.4 | 225.4 | 220.4 | YES
| NG | 14 | 13 | 13 | 9 | 104.6 | 10.71 | 50 | 88.7 | 5.9 | [5 empty] | NO | TR_A sim: not converged
3 | OK | 11 | 12 | 18 | 9 | 130.3 | 5.15 | 50 | 88.7 | 5.9 | 68.7 | 0 | 218 | 9751192927380648 | 218 | YES
4 | OK | 13 | 0 | 0 | 9 | 142 | 9.43 | 50 | 88.7 | 5.9 | 52.2 | 10.3 | 220.4 | 224.8 | 220.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 54-005321
TR_B (available) | 65-026079
TR_A Rated kVA | 30
TR_B Rated kVA | 250
TR_A Baseline Loading% | 88.7
TR_B Baseline Loading% | 5.9
Total Scenarios Evaluated | 7
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 8
Switch Child Node | 14
Tie Node (TR_A side) | 16
Tie Node (TR_B side) | 9
Tie Line Distance (m) | 84.5
Load Transferred (kW) | 10.98
TR_A Loading After (%) | 42.1
TR_B Loading After (%) | 11.1
Minimum Voltage (V) | 222.3