## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 11 | 22 | 31 | 12 | 151.4 | 20.56 | 50 | 84.2 | 24.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 22 | 23 | 31 | 12 | 151.4 | 20.17 | 50 | 84.2 | 24.5 | [5 empty] | NO | TR_B sim: not converged
| NG | 23 | 24 | 31 | 12 | 151.4 | 17.85 | 50 | 84.2 | 24.5 | 14.4 | 75.6 | 228.5 | 165.3 | 165.3 | NO
| NG | 24 | 12 | 31 | 12 | 151.4 | 17.85 | 50 | 84.2 | 24.5 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 24.5% (degenerate)
| NG | 12 | 25 | 31 | 12 | 151.4 | 11.54 | 50 | 84.2 | 24.5 | 38.6 | 54.4 | 224.2 | 193.8 | 193.8 | NO
| NG | 25 | 26 | 31 | 12 | 151.4 | 10.09 | 50 | 84.2 | 24.5 | 44.2 | 50.2 | 223.2 | 199.7 | 199.7 | NO
| NG | 26 | 27 | 31 | 12 | 151.4 | 8.76 | 50 | 84.2 | 24.5 | 49.4 | 46.4 | 221.7 | 207.4 | 207.4 | NO
| NG | 27 | 28 | 31 | 12 | 151.4 | 8.22 | 50 | 84.2 | 24.5 | 51.5 | 45 | 220.8 | 207.9 | 207.9 | NO
| NG | 28 | 4 | 31 | 12 | 151.4 | 8.11 | 50 | 84.2 | 24.5 | 52 | 44.7 | 220.8 | 208.5 | 208.5 | NO
1 | OK | 4 | 5 | 31 | 12 | 151.4 | 3.83 | 50 | 84.2 | 24.5 | 69 | 33.8 | 213.1 | 213.1 | 213.1 | YES
2 | OK | 5 | 29 | 31 | 12 | 151.4 | 3.16 | 50 | 84.2 | 24.5 | 71.6 | 32.1 | 213.2 | 216.5 | 213.2 | YES
3 | OK | 29 | 18 | 31 | 12 | 151.4 | 2.16 | 50 | 84.2 | 24.5 | 75.5 | 29.6 | 213.3 | 221.3 | 213.3 | YES
4 | OK | 18 | 19 | 31 | 12 | 151.4 | 1.98 | 50 | 84.2 | 24.5 | 76.2 | 29.2 | 213.3 | 222.1 | 213.3 | YES
5 | ** OPTIMAL ** | 19 | 30 | 31 | 12 | 151.4 | 1.86 | 50 | 84.2 | 24.5 | 76.7 | 28.9 | 213.3 | 222.5 | 213.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 54-006108
TR_B (available) | 53-010391
TR_A Rated kVA | 30
TR_B Rated kVA | 50
TR_A Baseline Loading% | 84.2
TR_B Baseline Loading% | 24.5
Total Scenarios Evaluated | 14
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 19
Switch Child Node | 30
Tie Node (TR_A side) | 31
Tie Node (TR_B side) | 12
Tie Line Distance (m) | 151.4
Load Transferred (kW) | 1.86
TR_A Loading After (%) | 76.7
TR_B Loading After (%) | 28.9
Minimum Voltage (V) | 213.3